## CurveComparison
Variable Volume Fan Curve Coefficient Comparison
Power is greater of PowerMin or PLR = A + B*FanRatio + C*FanRatio^2 + D*FanRatio^3
Sources:
| ASHRAE 90.1 PRM | PNNL, "BuildingsANSI/ASHRAE/IES Standard 90.1-2016 Performance Rating Method Reference Manual," September 2017
| CEC 2003 VAV | California Energy Commision, "Advanced Variable Air Volume System Design Guide," October 2003.
| Curve Name | Multi Zone VAV with Airfoil or Backward Incline riding the curve | Multi Zone VAV with Airfoil or Backward Incline with inlet vanes | Multi Zone VAV with Forward Curved fans riding the curve | Multi Zone VAV with Forward Curved with inlet vanes | Multi Zone VAV with vane-axial with variable pitch blades | Multi Zone VAV with VSD and fixed SP setpoint | Multi zone VAV with static pressure reset | Single zone VAV fan | Typical VSD Fan | No SP Reset VSD Fan
| Source | ASHRAE 90.1 PRM | ASHRAE 90.1 PRM | ASHRAE 90.1 PRM | ASHRAE 90.1 PRM | ASHRAE 90.1 PRM | ASHRAE 90.1 PRM | ASHRAE 90.1 PRM | ASHRAE 90.1 PRM | CEC 2003 VAV | CEC 2003 VAV
| Notes | [6 empty] | OpenStudio Default
| Notes | [5 empty] | ASHRAE 90.1 App.G baseline | ASHRAE 90.1 PRM baseline systems 5-8 | ASHRAE 90.1 PRM baseline system 11
| A | 0.1631 | 0.9977 | 0.1224 | 0.3038 | 0.1639 | 0.0013 | 0.04076 | 0.027828 | 0.047183 | 0.070429
| B | 1.5901 | -0.659 | 0.612 | -0.7608 | -0.4016 | 0.147 | 0.088045 | 0.026583 | 0.13054 | 0.38533
| C | -0.8817 | 0.9547 | 0.5983 | 2.2729 | 1.9909 | 0.9506 | -0.072926 | -0.087069 | -0.11729 | -0.46086
| D | 0.1281 | -0.2936 | -0.3334 | -0.8169 | -0.7541 | -0.0998 | 0.94374 | 1.0309 | 0.94031 | 1.0092
| PowerMin | 70% | 50% | 30% | 30% | 20% | 20% | 10% | 10% | 10% | 10%
FanRatio
| 0% | 0.7 | 0.9977 | 0.3 | 0.3038 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1
| 1% | 0.7 | 0.99121 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1
| 2% | 0.7 | 0.9849 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1
| 3% | 0.7 | 0.97878 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1
| 4% | 0.7 | 0.97285 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1
| 5% | 0.7 | 0.9671 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1
| 6% | 0.7 | 0.96153 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1
| 7% | 0.7 | 0.95615 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1
| 8% | 0.7 | 0.95094 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1
| 9% | 0.7 | 0.94591 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.10211
| 10% | 0.7 | 0.94105 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.10536
| 11% | 0.7 | 0.93637 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.10858
| 12% | 0.7 | 0.93186 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.11178
| 13% | 0.7 | 0.92752 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.11495
| 14% | 0.7 | 0.92335 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.11811
| 15% | 0.7 | 0.91934 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.12127
| 16% | 0.7 | 0.9155 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.12442
| 17% | 0.7 | 0.91182 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.12757
| 18% | 0.7 | 0.9083 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.13074
| 19% | 0.7 | 0.90494 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.13393
| 20% | 0.7 | 0.90174 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.13713
| 21% | 0.7 | 0.89869 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.14037
| 22% | 0.7 | 0.8958 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.14364
| 23% | 0.7 | 0.89306 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.14695
| 24% | 0.7 | 0.89047 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.15031
| 25% | 0.7 | 0.88803 | 0.30758 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.15373
| 26% | 0.7 | 0.88574 | 0.31611 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1572
| 27% | 0.7 | 0.88359 | 0.32469 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.16074
| 28% | 0.7 | 0.88158 | 0.33335 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.16434
| 29% | 0.7 | 0.87972 | 0.34207 | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.16803
| 30% | 0.7 | 0.878 | 0.35085 | 0.3 | 0.20224 | 0.2 | 0.1 | 0.1 | 0.10118 | 0.1718
| 31% | 0.7 | 0.87641 | 0.35968 | 0.3 | 0.20826 | 0.2 | 0.1 | 0.1 | 0.10439 | 0.17566
| 32% | 0.7 | 0.87496 | 0.36858 | 0.3 | 0.21455 | 0.2 | 0.1 | 0.1 | 0.10776 | 0.17961
| 33% | 0.7 | 0.87365 | 0.37753 | 0.3 | 0.22108 | 0.2 | 0.1 | 0.1 | 0.11128 | 0.18367
| 34% | 0.7 | 0.87246 | 0.38654 | 0.3 | 0.22786 | 0.2 | 0.1 | 0.1 | 0.11497 | 0.18783
| 35% | 0.7 | 0.87141 | 0.3956 | 0.3 | 0.23489 | 0.2 | 0.10311 | 0.1 | 0.11882 | 0.19211
| 36% | 0.7 | 0.87049 | 0.4047 | 0.3 | 0.24216 | 0.2 | 0.10704 | 0.1 | 0.12285 | 0.19651
| 37% | 0.7 | 0.8697 | 0.41386 | 0.3 | 0.24966 | 0.2 | 0.11116 | 0.1 | 0.12706 | 0.20103
| 38% | 0.7 | 0.86903 | 0.42306 | 0.3 | 0.2574 | 0.2 | 0.11547 | 0.1 | 0.13145 | 0.20568
| 39% | 0.7 | 0.86848 | 0.4323 | 0.30434 | 0.26536 | 0.2 | 0.11999 | 0.1 | 0.13603 | 0.21048
| 40% | 0.7 | 0.86806 | 0.44159 | 0.31086 | 0.27354 | 0.20581 | 0.12471 | 0.1 | 0.14081 | 0.21541
| 41% | 0.7 | 0.86776 | 0.45092 | 0.31764 | 0.28194 | 0.21449 | 0.12964 | 0.1 | 0.1458 | 0.2205
| 42% | 0.7 | 0.86758 | 0.46028 | 0.32468 | 0.29055 | 0.22333 | 0.13479 | 0.10001 | 0.15099 | 0.22574
| 43% | 0.7 | 0.86751 | 0.46968 | 0.33197 | 0.29937 | 0.23234 | 0.14017 | 0.10512 | 0.15639 | 0.23115
| 44% | 0.70296 | 0.86756 | 0.47911 | 0.33949 | 0.3084 | 0.24151 | 0.14577 | 0.11049 | 0.16201 | 0.23672
| 45% | 0.71177 | 0.86772 | 0.48857 | 0.34726 | 0.31762 | 0.25085 | 0.15161 | 0.1161 | 0.16786 | 0.24247
| 46% | 0.72045 | 0.868 | 0.49807 | 0.35526 | 0.32704 | 0.26035 | 0.15769 | 0.12198 | 0.17394 | 0.24839
| 47% | 0.72898 | 0.86838 | 0.50759 | 0.36349 | 0.33664 | 0.27002 | 0.16401 | 0.12812 | 0.18025 | 0.25451
| 48% | 0.73737 | 0.86887 | 0.51714 | 0.37195 | 0.34644 | 0.27984 | 0.17059 | 0.13454 | 0.18681 | 0.26081
| 49% | 0.74562 | 0.86947 | 0.52671 | 0.38062 | 0.35641 | 0.28983 | 0.17742 | 0.14124 | 0.19361 | 0.26732
| 50% | 0.75374 | 0.87018 | 0.5363 | 0.38951 | 0.36656 | 0.29997 | 0.18452 | 0.14822 | 0.20067 | 0.27403
| 51% | 0.76171 | 0.87098 | 0.54591 | 0.39861 | 0.37688 | 0.31028 | 0.19188 | 0.15549 | 0.20799 | 0.28095
| 52% | 0.76955 | 0.87189 | 0.55554 | 0.40791 | 0.38737 | 0.32075 | 0.19952 | 0.16306 | 0.21557 | 0.28808
| 53% | 0.77725 | 0.87289 | 0.56519 | 0.41742 | 0.39803 | 0.33138 | 0.20744 | 0.17094 | 0.22342 | 0.29544
| 54% | 0.78482 | 0.874 | 0.57485 | 0.42711 | 0.40884 | 0.34216 | 0.21564 | 0.17913 | 0.23154 | 0.30303
| 55% | 0.79225 | 0.8752 | 0.58452 | 0.437 | 0.4198 | 0.3531 | 0.22414 | 0.18763 | 0.23995 | 0.31086
| 56% | 0.79955 | 0.87649 | 0.5942 | 0.44707 | 0.43092 | 0.3642 | 0.23293 | 0.19646 | 0.24864 | 0.31892
| 57% | 0.80672 | 0.87788 | 0.60388 | 0.45733 | 0.44218 | 0.37546 | 0.24203 | 0.20561 | 0.25762 | 0.32723
| 58% | 0.81375 | 0.87936 | 0.61358 | 0.46775 | 0.45358 | 0.38687 | 0.25143 | 0.2151 | 0.26691 | 0.33579
| 59% | 0.82065 | 0.88092 | 0.62327 | 0.47835 | 0.46511 | 0.39844 | 0.26115 | 0.22493 | 0.2765 | 0.34462
| 60% | 0.82742 | 0.88257 | 0.63297 | 0.48911 | 0.47678 | 0.41016 | 0.27118 | 0.23511 | 0.28639 | 0.3537
| 61% | 0.83406 | 0.88431 | 0.64267 | 0.50004 | 0.48857 | 0.42204 | 0.28154 | 0.24564 | 0.2966 | 0.36306
| 62% | 0.84057 | 0.88613 | 0.65237 | 0.51112 | 0.50049 | 0.43407 | 0.29223 | 0.25654 | 0.30714 | 0.3727
| 63% | 0.84695 | 0.88804 | 0.66206 | 0.52235 | 0.51252 | 0.44625 | 0.30326 | 0.2678 | 0.318 | 0.38262
| 64% | 0.8532 | 0.89002 | 0.67174 | 0.53372 | 0.52467 | 0.45858 | 0.31463 | 0.27943 | 0.32919 | 0.39283
| 65% | 0.85933 | 0.89208 | 0.68142 | 0.54524 | 0.53692 | 0.47107 | 0.32635 | 0.29144 | 0.34071 | 0.40333
| 66% | 0.86533 | 0.89422 | 0.69109 | 0.55689 | 0.54928 | 0.48371 | 0.33842 | 0.30383 | 0.35259 | 0.41414
| 67% | 0.8712 | 0.89643 | 0.70074 | 0.56868 | 0.56174 | 0.4965 | 0.35086 | 0.31662 | 0.36481 | 0.42525
| 68% | 0.87695 | 0.89872 | 0.71038 | 0.58059 | 0.57429 | 0.50944 | 0.36365 | 0.3298 | 0.37738 | 0.43668
| 69% | 0.88257 | 0.90107 | 0.72001 | 0.59262 | 0.58693 | 0.52253 | 0.37682 | 0.34338 | 0.39032 | 0.44842
| 70% | 0.88808 | 0.9035 | 0.72961 | 0.60476 | 0.59966 | 0.53576 | 0.39036 | 0.35738 | 0.40362 | 0.46049
| 71% | 0.89345 | 0.90599 | 0.7392 | 0.61702 | 0.61248 | 0.54915 | 0.40428 | 0.37179 | 0.41729 | 0.4729
| 72% | 0.89871 | 0.90855 | 0.74876 | 0.62939 | 0.62536 | 0.56268 | 0.4186 | 0.38662 | 0.43134 | 0.48564
| 73% | 0.90385 | 0.91117 | 0.7583 | 0.64186 | 0.63832 | 0.57636 | 0.4333 | 0.40188 | 0.44577 | 0.49872
| 74% | 0.90886 | 0.91386 | 0.76781 | 0.65442 | 0.65135 | 0.59019 | 0.4484 | 0.41757 | 0.4606 | 0.51216
| 75% | 0.91376 | 0.91661 | 0.77729 | 0.66708 | 0.66445 | 0.60416 | 0.46391 | 0.43371 | 0.47581 | 0.52595
| 76% | 0.91854 | 0.91941 | 0.78674 | 0.67982 | 0.6776 | 0.61828 | 0.47983 | 0.45029 | 0.49142 | 0.5401
| 77% | 0.9232 | 0.92227 | 0.79616 | 0.69264 | 0.6908 | 0.63254 | 0.49616 | 0.46732 | 0.50744 | 0.55462
| 78% | 0.92774 | 0.92519 | 0.80555 | 0.70555 | 0.70406 | 0.64694 | 0.51292 | 0.48482 | 0.52388 | 0.56952
| 79% | 0.93217 | 0.92816 | 0.8149 | 0.71852 | 0.71736 | 0.66149 | 0.5301 | 0.50277 | 0.54072 | 0.58479
| 80% | 0.93648 | 0.93118 | 0.82421 | 0.73156 | 0.7307 | 0.67619 | 0.54772 | 0.5212 | 0.55799 | 0.60045
| 81% | 0.94068 | 0.93426 | 0.83348 | 0.74467 | 0.74407 | 0.69102 | 0.56577 | 0.54011 | 0.57569 | 0.61651
| 82% | 0.94476 | 0.93738 | 0.84271 | 0.75783 | 0.75748 | 0.706 | 0.58427 | 0.5595 | 0.59382 | 0.63296
| 83% | 0.94873 | 0.94055 | 0.8519 | 0.77104 | 0.77092 | 0.72111 | 0.60322 | 0.57938 | 0.61239 | 0.64981
| 84% | 0.95258 | 0.94376 | 0.86103 | 0.78431 | 0.78438 | 0.73637 | 0.62262 | 0.59975 | 0.63141 | 0.66708
| 85% | 0.95633 | 0.94701 | 0.87012 | 0.79761 | 0.79785 | 0.75177 | 0.64248 | 0.62063 | 0.65087 | 0.68476
| 86% | 0.95996 | 0.95031 | 0.87916 | 0.81095 | 0.81134 | 0.76731 | 0.66281 | 0.64202 | 0.6708 | 0.70287
| 87% | 0.96348 | 0.95365 | 0.88815 | 0.82433 | 0.82484 | 0.78298 | 0.68362 | 0.66392 | 0.69118 | 0.7214
| 88% | 0.9669 | 0.95702 | 0.89708 | 0.83774 | 0.83835 | 0.79879 | 0.7049 | 0.68634 | 0.71203 | 0.74037
| 89% | 0.9702 | 0.96043 | 0.90596 | 0.85116 | 0.85185 | 0.81474 | 0.72666 | 0.70929 | 0.73335 | 0.75978
| 90% | 0.9734 | 0.96387 | 0.91477 | 0.86461 | 0.86535 | 0.83083 | 0.74892 | 0.73277 | 0.75516 | 0.77964
| 91% | 0.97649 | 0.96735 | 0.92353 | 0.87807 | 0.87884 | 0.84706 | 0.77167 | 0.75679 | 0.77744 | 0.79994
| 92% | 0.97947 | 0.97086 | 0.93223 | 0.89154 | 0.89232 | 0.86341 | 0.79492 | 0.78135 | 0.80022 | 0.82071
| 93% | 0.98235 | 0.97439 | 0.94086 | 0.90501 | 0.90578 | 0.87991 | 0.81867 | 0.80647 | 0.82349 | 0.84194
| 94% | 0.98512 | 0.97795 | 0.94942 | 0.91848 | 0.91921 | 0.89654 | 0.84294 | 0.83215 | 0.84727 | 0.86365
| 95% | 0.98779 | 0.98154 | 0.95792 | 0.93194 | 0.93262 | 0.9133 | 0.86773 | 0.85839 | 0.87155 | 0.88583
| 96% | 0.99036 | 0.98515 | 0.96634 | 0.9454 | 0.946 | 0.9302 | 0.89303 | 0.8852 | 0.89634 | 0.90849
| 97% | 0.99282 | 0.98879 | 0.9747 | 0.95883 | 0.95934 | 0.94722 | 0.91887 | 0.91258 | 0.92165 | 0.93164
| 98% | 0.99518 | 0.99244 | 0.98297 | 0.97225 | 0.97264 | 0.96439 | 0.94525 | 0.94055 | 0.94749 | 0.95529
| 99% | 0.99744 | 0.99611 | 0.99118 | 0.98564 | 0.98589 | 0.98168 | 0.97216 | 0.96911 | 0.97385 | 0.97944
| 100% | 0.9996 | 0.9998 | 0.9993 | 0.999 | 0.9991 | 0.9991 | 0.99962 | 0.99826 | 1.0008 | 1.0041
This measure changes the polynomial curve coefficients and minimum fan power that define the fan power performance curve for Fan:VariableSpeed objects in EnergyPlus.
Curve coefficients come from ASHRAE Standard 90.1-2016 Performance Rating Method Reference Manual Table 50 Fan Curve Default Values (identical to ASHRAE 90.1-2010 PRM Reference Manual Table 47) [1]. The OpenStudio default is "Multi-zone VAV with static pressure reset", which is the ASHRAE 90.1 PRM baseline for systems 5-8. The ASHRAE 90.1 PRM baseline for system 11 is "Single zone VAV fan" representing a perfect static pressure reset. The ASHRAE 90.1 Appendix G Table G3.1.3.15 default is "Multi Zone VAV with VSD and fixed SP setpoint", which assumes no static pressure reset, and is sourced separately [4] (identical across ASHRAE 90.1-2007,2010,2013,2016). Note that the ASHRAE 90.1 PRM baseline is the OpenStudio default and is different from the ASHRAE 90.1 Appendix G baseline.
The OpenStudio default is identical to the "Good SP Reset VSD Fan" originally sourced from a 2003 California Energy Commission report, "Advanced Variable Air Volume System Design Guide" Appendix 5 - DOE-2 Fan Curves [2], which were created by Jeff Stein and Mark Hydeman from their fan curve model, detailed in "Development and Testing of the Characteristic Curve Fan Model" ASHRAE Transactions. 2004, Vol. 110 Issue 1, p347-356. 10p. [3]. This measure also includes curve coefficients for "No SP Reset VSD Fan", "Typical VSD Fan", and "Perfect SP Reset VSD Fan" (identical to "Single zone VAV fan") as detailed in the 2003 CEC report.
Fan power is calculated as the Part Load Ratio (PLR) times rated fan power. PLR is greater of:
PLR = A + B*FanRatio + C*FanRatio^2 + D*FanRatio^3
PLR = PowerMin
PLR = Ratio of fan power at part load conditions to full load fan power
PowerMin = Minimum fan power ratio
FanRatio = Ratio of air flow rate at part-load to full load air flow rate in cfm
A,B,C,D = Coefficients for the fan power curve
Sources:
- [1] PNNL, "BuildingsANSI/ASHRAE/IES Standard 90.1-2016 Performance Rating Method Reference Manual," September 2017.
- [2] California Energy Commision, "Advanced Variable Air Volume System Design Guide," October 2003.
- [3] - Jeff Stein and Mark Hydeman, "Development and Testing of the Characteristic Curve Fan Model," ASHRAE Transactions. 2004, Vol. 110 Issue 1, p347-356. 10p. Available online at (http://www.taylor-engineering.com/Websites/taylorengineering/articles/ASHRAE_Symposium_AN-04-3-1_Characteristic_Curve_Fan_Model.pdf)
- [4] ANSI/ASHRAE/IES Standard 90.1-2016 - Energy Standard for Buildings Except Low-Rise Residential
California Energy Commission, "2016 Nonresidential Compliance Manual," November 2015.