## About
Residential Electrical Service Upgrade Decision Tool - Individual Home Tool
ABOUT
This tool was funded through the CalNEXT program, the California statewide electric emerging technologies program. TRC led the development of the tool, in collaboration with Build it Green and SPUR.
For more information on background research and design of the tool, please see the Final CalNEXT report available on the CalNEXT website: Approved Projects - CalNEXT
DISCLAIMER
The CalNEXT program is designed and implemented by Cohen Ventures, Inc., DBA Energy Solutions (“Energy Solutions”). Southern California Edison Company, on behalf of itself, Pacific Gas and Electric Company, and San Diego Gas & Electric® Company (collectively, the “CA Electric IOUs”), has contracted with Energy Solutions for CalNEXT. CalNEXT is available in each of the CA Electric IOU’s service territories. Customers who participate in CalNEXT are under individual agreements between the customer and Energy Solutions or Energy Solutions’ subcontractors (Terms of Use). The CA Electric IOUs are not parties to, nor guarantors of, any Terms of Use with Energy Solutions. The CA Electric IOUs have no contractual obligation, directly or indirectly, to the customer. The CA Electric IOUs are not liable for any actions or inactions of Energy Solutions, or any distributor, vendor, installer, or manufacturer of product(s) offered through CalNEXT. The CA Electric IOUs do not recommend, endorse, qualify, guarantee, or make any representations or warranties (express or implied) regarding the findings, services, work, quality, financial stability, or performance of Energy Solutions or any of Energy Solutions’ distributors, contractors, subcontractors, installers of products, or any product brand listed on Energy Solutions’ website or provided, directly or indirectly, by Energy Solutions. If applicable, prior to entering into any Terms of Use, customers should thoroughly review the terms and conditions of such Terms of Use so they are fully informed of their rights and obligations under the Terms of Use, and should perform their own research and due diligence, and obtain multiple bids or quotes when seeking a contractor to perform work of any type.

## Instructions & Info
TOOL PURPOSE AND USERS:
This tool is designed for contractors, in collaboration with single family homeowners, to guide decision-making and strategies for home electrification projects while minimizing or avoiding the need to upgrade the electrical panel or service capacity. Homeowners should be guiding the electrification priorities for the project, and qualified contractors will need to verify the accuracy of information in the tool and the conditions at the project site. Standard practice electrification choices frequently require panel upgrades, but this tool will help identify opportunities to optimize electrification strategies to avoid unnecessary panel and service upgrades.
The tool makes estimated National Electrical Code (NEC) load calculations to determine the possible need to upgrade the main electrical panel and service to the existing home, based on user inputs. If the initial inputs indicate a need to upgrade the panel, the tool provides three levels of optimization options that may allow for home electrification without a panel and service upgrade.
Read through the recommended procedure below for more details, and review the guidance on each tab carefully to understand the potential compromises of the different options. Enter information in each tab as completely as possible, working through the tabs from left to right.
RECOMMENDED PROCEDURE
1. Start from the blank template file for each new project. Create a new copy ("save as") of the tool file with a unique project name.
2. "Property Information" tab - Enter basic property details on this tab. County, year of construction, square feet of living area, panel voltage rating, and existing main panel disconnect rating must be entered to accurately calculate default loads and panel results. Other inputs on this tab are optional. Review detailed guidance on the tab for more information.
3. "Existing Systems and Loads" tab - Enter all existing building systems and loads in this tab. The tool will assume certain default values for HVAC and other building systems based on home characteristics and typical practice. Users should provide actual nameplate values for system sizing wherever available. Review and update information in the “Other Existing Electrical Loads” section to accurately account for existing conditions in the home. Review detailed guidance on the tab for more information.
4. "Electrification Upgrades" tab - Enter all building electrification goals on this tab. This tab will default to show all existing gas/propane appliances as electrified, AND will show the addition of one EV charger. Users can adjust the electrification goals as needed to match project objectives. As with the previous tab, the tool assumes default values for all electrified systems. Default systems assume 1-for-1 service level replacements and typical practice for appliance choices. Users should input any actual values for preferred systems and appliances if those are known. Review detailed guidance on the tab for more information.
5. Check the "Panel Impacts and Rec’s" tab for initial results - The graph on this tab illustrates the impact of the choices on the "Electrification Upgrades" tab on the electrical panel. Segments of the bar chart shown in red indicate that the selected loads exceed the existing panel capacity. If the electrification upgrades exceed existing panel capacity, users can explore optimization options as outlined below to reduce the overall load and achieve the upgrades within existing capacity. Work through the optimization tabs sequentially, and check back to the Electrical Panel Inputs tab after each one to determine whether the selected options will allow for all upgrades within the existing capacity.
6. "Opt. 1 - Low-Power Appliances" tab - This tab allows the user to select power-efficient appliance options as alternatives to the default electrification choices on the Electrification Goals tab. Examples of power-efficient appliances include 120v heat pump water heaters, combined washer-dryer appliances, and lower amperage electric vehicle chargers, among others. Review detailed guidance on the tab for more information. After selecting low-power appliance options, check the Panel Impacts and Rec’s tab to assess the results.
7. "Opt. 2 – Right-Size HVAC" tab - This tab allows the user to adjust the HVAC system size (to account for building envelope improvements or to correct for previously oversized systems), and to remove any backup strip heat (typically installed by default, but not necessary in most California climate zones). Review detailed guidance on the tab for more information. After adjusting HVAC system options, check the Panel Impacts and Rec’s tab to assess the results.
8. "Opt.3 - Panel Load Mgmt" tab - If optimization options in the previous two tabs are not sufficient to bring the overall load within the existing electrical panel capacity, this tab allows users to choose from several panel load management strategies. Load management options on this tab are circuit sharing, dynamic vehicle chargers (that automatically adjust the charging load based on available capacity), and smart electrical panels. The user is required to select one of these three options to show the results in the Electrical Panel Impacts tab. Review detailed guidance on the tab for more information. After selecting a Panel Load Management option, check the Panel Impacts and Rec’s tab to assess the results.
9. Determine your electrification plan - Review the "Panel Impacts and Rec’s" tab for the results of all the selections. The Measure Tracking Table at the bottom of the tab shows all of the system and optimization selections the user has made. Ideally the selections will allow for whole home electrification within the existing panel capacity. If the selections do not fit within the existing capacity, the description on the Panel Impacts and Rec’s tab indicates the panel size needed to accommodate the user selections. Continue adjusting the selections in the previous tabs as needed to achieve the optimal solution for the home.
10. To reset all selections and options in the tool, start from a new blank template.
Additional Guidance on Home Electrification and NEC Calculation Procedures
Home electrification is the process of replacing combustion-powered (natural gas, propane, fuel oil, etc.) systems and appliances with electric-powered alternatives. However, adding new electrical loads will likely cause an increase in power demand on the existing home electrical system. Contractors must calculate the new electrical loads to determine whether the existing utility service and home electrical panel capacity are sufficient to meet the new electrical demand. The required calculations are defined through several different sections of the National Electrical Code (NEC), specifically Section 220.83, which focuses on demand calculations when adding electrical load to an existing home.
Because the calculations are stipulated through the NEC, there is a relatively clear interpretation of the required load calculations. This allows a calculator tool like this one to predict the outcomes of detailed NEC calculations for the proposed electrification and any potential strategies to reduce to reduce the overall load.
Alternatively, NEC Section 220.87 describes a method that allows contractors to use metered energy demand data (AMI data) to determine the remaining electrical service capacity at a home. This section applies a factor of 1.25 to the maximum metered demand data over a year, then adds the new load to calculate service requirements. This tool does not address the 220.87 approach for a few reasons. Not all permitting agencies accept the 220.87 approach on permit applications. In some cases, past energy data may not be available. Section 220.87 can also lead to a double count of loads in some cases because it treats historical loads and any new loads as fully coincident. Because 220.87 greatly simplifies the process of calculating existing service demand, contractors pursuing this method may be less likely to need a tool like this to determine remaining capacity and electrification options. However, contractors pursuing the 220.87 method can still use this tool to explore and assess how different optimization strategies could reduce the total new loads and optimize existing service capacity in a home electrification project.

## Notes
This space provided to record notes

## Property Information
Enter Home Information Below
Legend
Input expected (default value may be shown)
Input selected for "N" or similar negative input chosen
Optional inputs
Calculation output values / no inputs permitted
|  |  |  | Text | This is guidance information text.
| Customer Information |  | Notes:
| Name | Jane Doe
| Address | 123 Any Street
Address 2
| City | Any Town
| State | California
| County | Sacramento | This is used for BTUh calculations for heating and cooling load.
| ZIP Code | 95670
Residence Information
| Type of residence | Detached SF
| Year of construction | Before - 1975 | This is used to establish the likely level of tightness and insulation in the home.
| Square feet living space | 1500 | Gross conditioned space square footage (not including garage).
| Local Electrical Utility | Local POU
Existing Electrical Panel Information
| Panel Name | Main Panel
| Panel Voltage Rating | 240/120 V
| Existing Main Panel Disconnect Rating | 100 | This amperage is the starting point for the load calculations.
| Size of Panel (number of slots) | 24
PROPERTY INFORMATION
Input the location of the property and other information that is available for the property.
The vintage of the building helps determine how energy efficient the assumptions are for the existing HVAC system, and will carry through to the asssumptions for an upgraded HVAC system is no manual inputs are made to the system conditions.
The living area square footage is related to the HVAC sizing and also the NEC assumptions for the wattage required for lighting and other general loads in the house.

## Existing Systems and Loads
Enter Existing Building System Information Below
Legend
Input expected (default value may be shown)
Input selected for "N" or similar negative input chosen
Optional inputs
Calculation output values / no inputs permitted
[11 empty] | Text | This is guidance information text.
[5 empty] | Electrical Characteristics of System |  |  |  |  | Existing Loads
Select 'Y' if System Exists in Home | Description | Type | Main Energy Source | Assumed Size | Default Voltage | Assumed Nameplate Power (VA) | Use Default? | Manual Voltage | Manual Amperage | Volt-Amps (VA)
Y | Space Heating | Central forced air | NG, Propane, Fuel oil | 3 | 120 | 100 | Y |  |  | 100 | Sized up to the nearset 1/2 Ton. Adjust for actual if known for a more accurate calculation. If using central air, the AHU is included two rows down and backup strip heat is three rows down.
Y | Space Cooling | Central forced air | Electric | 2.5 | 240 | 5100 | Y |  |  | 5100 | Sized up to the nearset 1/2 Ton. Adjust for actual if known for a more accurate calculation.
Y | Ventilation | Air Handler | Electric | 600 | 240 | 600 | Y |  |  | 600 | AHU fan and controls only. Backup strip heat is the next line item.
N | Reserved for HP Backup | Strip Heat | Electric |  |  |  | Y |  |  |  | Will normally be part of the AHU, and typically only included if a Heat Pump is installed. Assumes strip heat is sized for 75% of the house heating load.
Y | Clothes Washer | Side by Side Full size | Electric | 480 | 120 | 480 | Y |  |  | 480
Y | Clothes Dryer | Side by Side Full size | NG, Propane | 480 | 120 | 480 | Y |  |  | 480 | If electric, must use nameplate if higher than 5000 VA
Y | Range (cooktop and oven) | 30" CT/Oven | NG, Propane | 480 | 120 | 480 | Y |  |  | 480 | If electric, must use nameplate if higher than 8000 VA
N | Oven (seperates) - Single | [5 empty] | Y |  |  |  | If electric, must use nameplate if higher than 4800 VA
N | Oven (seperates) - Double | [5 empty] | Y |  |  |  | If electric, must use nameplate if higher than 8000 VA
N | Cooktop (seperates) | [5 empty] | Y |  |  |  | If electric, must use nameplate if higher than 3600 VA
Y | Water Heater | Tank < 50gal | NG, Propane | 305 | 120 | 305 | Y |  |  | 305
N | Water heater 2 | [5 empty] | Y
N | EV Charger | [5 empty] | Y
N | Other Large Loads 1 | [9 empty] | Data must be input manually for the Other loads
N | Other Large Loads 2 | [9 empty] | Data must be input manually for the Other loads
N | Other Large Loads 3 | [9 empty] | Data must be input manually for the Other loads
Other Existing Electric Loads (not impacted by electrification retrofit)
General Loads
| Description | Notes | Quantity |  | Default Voltage | Default Power | Use Default? |  | Manual Volt-Amps (VA) | Volt-Amps (VA)
Req'd | Lighting Circuits |  |  |  | 120 | 3 | Y |  |  | 4500 | Must be at least 3 W/sf
Req'd | Small Appliance Circuits (2 circuits minimum) |  | 2 |  | 120 | 1500 | Y |  |  | 3000 | Must have at least two circuits
Req'd | Laundry Circuit (1500 VA minimum) |  | 1 |  | 120 | 1500 | Y |  |  | 1500 | Must have at least one 1500W circuit IF THERE IS A LAUNDRY
Fixed Appliances
Exists in Home? | Description | Notes | Quantity |  | Default Voltage | Default Power | Use Default? |  | Manual Volt-Amps (VA) | Volt-Amps (VA)
Y | Refrigerator |  |  |  | 120 | 750 | Y |  |  | 750
Y | Garbage Disposal |  |  |  | 120 | 600 | Y |  |  | 600
Y | Dishwasher |  |  |  | 120 | 1200 | Y |  |  | 1200
Y | Microwave |  |  |  | 120 | 1500 | Y |  |  | 1500
Y | Kitchen Hood |  |  |  | 120 | 250 | Y |  |  | 250
Y | Bathroom Fan |  | 2 |  | 120 | 150 | Y |  |  | 300
N | Other Appliance 1 |  |  |  | 120
N | Other Appliance 2 |  |  |  | 120
N | Other Appliance 3 |  |  |  | 120
EXISTING BUILDING SYSTEMS
Input the existing building systems information on this tab. This information is broken into two categories; those that are likely to have electrification activity happen to them, those that will not have electrification upgrades.
Start with the left column of inputs and indicate "Y" or "N" on each of the building systems that are present in the existing (baseline) home. Most houses will have similar systems in them, so the default value for this column is a "Y" for some and a "N" for others, but they all can be changed if needed to suit the individual conditions of each residence.
After selecting a "Y"at the left, continue to the right and fill in the information from the drop-down options for each cell that is colored blue. The tool will make some basic reasonable assumptions of the electrical wattage of each device as the informatio on the type of device is selected. These default values can be used if they are accurate, but if the user have more exact information, the "Use Dafault?" column can be changed to "N" and manual information can be input into the cells on that row. This information shold be collected from the equipment nameplates or manufacturer's literature. DO NOT USE THE BREAKER SIZE FOR THE MANUAL AMPERAGE VALUE. The amperage should be pulled from the actual equipment labels or spec sheets. Using the breaker size will result in oversizing the load by at least 20%.
In the case of a device that is not primarily an electrical device (which uses natural gas or other main energy sources instead of electricity), most of them will still have an electrical connection for controls and/or fans, etc., so the wattage may be much lower, but is unlikely to be zero. This information is important because it enables a calculation of the existing building NEC load which becomes the baseline reference for the residence.
For the first four rows ("Space Heating", "Space Cooling", "Ventilation", and "Strip Heat Backup"), the loads are being treated seperate from each other because the energy source will possibly be different and in many cases, these will be wired through a control system that ensures both the heat and the AC are not on at the same time.
Most homes won't have more than one water heater and many will not have any "Other Large Loads", so those can be left blank unless they do occur in the residence. A common large load might be a spa. A spa can be entered in either the "Other Large Loads" or further down in the "Other Appliance" lines, however, only those in the "Other Large Loads" rows will be possible to modify as part of the electrification calculations. The loads in the "Other Appliance" rows are considered unchangable base loads.
OTHER EXISTING ELECTRICAL LOADS
These loads won't be changed through the electrification process so they are input on this tab and won't be optimized after this initial input.
The General Loads are dictated by the NEC calculation process and define lighting and receptacle circuits that are present in every house (and are not changable from an NEC calculation perspective). The number of appliance and laundry circuits is dicatated as minimums in the NEC code, so if the residence has more than these present, the number of circuits should be increased to reflect the actual conditions of the residence.
The remaining Fixed Appliance loads are intended for hard-wired appliances (not receptacle loads) and those items that are called out as requiring dedicated circuits. Extra lines are provided to add any additional items that aren't covered in the typical residence list.

## Electrification Upgrades
Select Building System Electrification Goals | [6 empty] | Legend
Input expected (default value may be shown)
Input selected for "N" or similar negative input chosen
Optional inputs
Calculation output values / no inputs permitted
[7 empty] | Text |  | This is guidance information text.
Default electrification systems reflect Standard Practice 1:1 replacements for the existing gas systems. If system details are known, enter in the Manual Input cells.
System details on this page may imply a need for panel and service upgrades. Use the optimization tabs to identify potential strategies to avoid panel upgrades.
Carries over from Systems and Loads if existing and not upgraded
[6 empty] | Electrical Characteristics of New System | [6 empty] | Load Calculation Values
Exists in Home? | Upgrade/Electrify System? | Description | Type | Main Energy Source | Assumed Size | Default Voltage | Assumed Nameplate Power (VA) | Use Default? |  | Manual Input Voltage | Manual Input Amperage | Volt-Amps (VA) | Type | Fuel Source | Volt-Amps (VA)
Y | Y | Space Heating | Central forced air | Electric - Heat Pump | 3 | 240 | 5760 | Y |  |  |  | 5760 | Central forced air | Electric - Heat Pump | 5760
Y | Y | Upgraded with Heating | Central forced air | Electric |  |  |  | Y
Y | Y | Ventilation | Air Handler | Electric | 500 | 240 | 500 | Y |  |  |  | 500 | Air Handler | Electric | 500
N | Y | Backup Strip Heat | Strip Heat | Electric | 7200 | 240 | 7200 | Y |  |  |  | 7200 | Strip Heat | Electric | 7200
Y | N | Clothes Washer | Side by Side Full size | Electric |  |  |  | Y |  |  |  |  | Side by Side Full size | Electric | 480
Y | Y | Clothes Dryer | Side by Side Full size | Electric - Heat Pump | 4000 | 240 | 4000 | Y |  |  |  | 4000 | Side by Side Full size | Electric - Heat Pump | 4000
Y | Y | Range (cooktop and oven) | 30" CT/Oven | Electric - Induction | 4800 | 240 | 4800 | Y |  |  |  | 4800 | 30" CT/Oven | Electric - Induction | 4800
N | N | Oven (seperates) - Single | [5 empty] | Y
N | N | Oven (seperates) - Double | [5 empty] | Y
N | N | Cooktop (seperates) | [5 empty] | Y
Y | Y | Water Heater | Tank < 50gal | Electric - Heat Pump | 4500 | 240 | 4500 | Y |  |  |  | 4500 | Tank < 50gal | Electric - Heat Pump | 4500
N | N | Water Heater 2 | [5 empty] | Y
N | Y | EV Charger | 50 Amp | Electric | 12000 | 240 | 12000 | Y |  |  |  | 12000 | 50 Amp | Electric | 12000
N | N | Other Large Loads 1 |  | Electric
N | N | Other Large Loads 2 |  | Electric
N | N | Other Large Loads 3 |  | Electric
Carries over from Systems and Loads if existing and not upgraded
BUILDING SYSTEMS ELECTRIFICATION
Mark each buiding system that will be upgraded/electrified with a "Y" in the second column from the left. The first column shows whether the system was already defined in the "Systems and Loads" tab as an existing system. If the system wasn't existing but it is being added to the home (an EV charger is a common example of this), you will see the "N" in the forst column, but placing a "Y" in the second will indicate this is a new system in the residence.
After selecting a "Y"at the left, continue to the right and fill in the information from the drop-down options for each cell that is colored blue. The tool will make some basic reasonable assumptions of the electrical wattage of each device as the information on the type of device is selected. These default values can be used if they are accurate, but if the user have more exact information, the "Use Dafault?" column can be changed to "N" and manual information can be input into the cells on that row. This information shold be collected from the equipment nameplates or manufacturer's literature. DO NOT USE THE BREAKER SIZE FOR THE MANUAL AMPERAGE VALUE. The amperage should be pulled from the actual equipment labels or spec sheets. Using the breaker size will result in oversizing the load by at least 20%.
All other loads not shown on this tab are not changing with the electrification activities and need no further inputs for the calculations.

## Panel Impacts and Rec's.
Panel Electrification Results
Panel Optimization Recommendations
| Baseline | Electrification Options | Opt #1 - Low Pwr Appliances | Opt #2 - Right-Size HVAC | Opt #3 - Load Mgmt
Baseline Amperage | 69.325
Amperage of Full Electrification |  | 173.7167
Amps Saved by Options |  |  | 0 | 0
% Amps Saved |  |  | 0% | 0%
Total Amperage |  | 173.7167 | 173.7167 | 173.7167
No Load Management selected
Measure Tracking Table
Optimization Options Selected
|  | Elect. Initial Upgrade | Opt #1 - Low Pwr Appliances | Opt #2 - Right-Size HVAC | Opt #3 - Load Mgmt
Space Heating |  | Y | N/A | N | Init. Upgrade
Air Conditioning |  | Y | N/A | N | Init. Upgrade
Ventilation |  | Y | N/A | N | Init. Upgrade
Strip Heat Backup |  | Y | N/A | N
Clothes Washer |  | N | N
Clothes Dryer |  | Y | N | Init. Upgrade | Init. Upgrade
Range (cooktop and oven) |  | Y | N | Init. Upgrade | Init. Upgrade
Oven (seperates) - Single |  | N
Oven (seperates) - Double |  | N
Cooktop (seperates) |  | N
Water Heater |  | Y | N | Init. Upgrade
Water Heater 2 |  | N
EV Charger |  | Y | N | N
Other Large Loads 1 |  | N | N/A | N/A | N/A
Other Large Loads 2 |  | N | N/A | N/A | N/A
Other Large Loads 3 |  | N | N/A | N/A | N/A
Circuit Sharing |  |  | N/A | N/A | N
Dynamic EV Charging |  |  | N/A | N/A | N
Smart Panel |  |  | N/A | N/A | N
Legend
|  | Y | This system has an upgrade or an optimization chosen at this step
|  | N | This system does not have an upgrade or an optimization chosen at this step
|  | Opt. 1 | This system has an upgrade or optimization, but it is being carried through this step
The existing main electrical panel is 100 Amps.
With all the electrification measures chosen in the 'Electrification Upgrades' tab, the minimum size electrical panel and service will need to be 200 Amps.
The current optimization measures are insufficient to lower the panel size below the 200 Amp size.
The electrification upgrades selected will require a panel and service upgrade, but follow the optimization options recommendations below to mitigate this impact.
Your current optimization selections exceed your existing panel capacity, and require an upgrade to a 200 Amp service. Consider making additional optimization selections, or proceed with a service upgrade.
Low Power Appliances - No LPA options are chosen. Go to the LPA tab and select options that are viable for the client.
Right Size HVAC - No HVAC options are chosen. Go to the HVAC tab and select options that are viable for the client if applicable through HVAC or envelope upgrades.
Load Management - No LM options are chosen. Go to the LM tab and select options that are viable for the client .
Note: All tool results and calculations must be confirmed by a qualified contractor, verifying conditions on site. Contractor to verify that selected strategies and calculation approach are allowable by the local permitting agency.
The optimized main electrical panel is 200 Amps.

## Opt. 1 - Low-Power Appliances
Proposed Building Systems Changes Round #1 - Low-Power Appliances
Consider a 120-volt Heat Pump water heater
Being Upgraded? | Modify to 120V Water Heater? | Description | Type | Main Energy Source | Assumed Size | Default Voltage | Default Power (VA) | Use Default? | Manual Voltage | Manual Amperage | Volt-Amps (VA) | Type | Fuel Source | Volt-Amps (VA)
Y | N | Water Heater | Tank < 50gal | Electric - HP 120V |  |  |  | Y |  |  |  | Tank < 50gal | Electric - Heat Pump | 4500
N | N | Water Heater 2 | [5 empty] | Y
Carries over from Systems and Loads -> Upgrades if not upgraded
Consider a Heat Pump Dryer (240/120V)
Being Upgraded? | Use a Heat Pump dryer? | Description | Type | Main Energy Source | Assumed Size | Default Voltage | Default Power (VA) | Use Default? | Manual Voltage | Manual Amperage | Volt-Amps (VA) | Type | Fuel Source | Volt-Amps (VA)
Y |  | Washer |  | Electric | 480 | 120 |  | Y |  |  |  | Side by Side Full size | Electric | 480
Y | N | Heat Pump dryer or combo | 120V Side by Side dryer | Electric - Heat Pump |  |  |  | Y |  |  |  | Side by Side Full size | Electric - Heat Pump | 4000
Carries over from Systems and Loads -> Upgrades if not upgraded
If you have kitchen 'seperates' (gas or electric), consider
using a single combined electric induction cooktop/oven…
Being Upgraded? | Use combined induction cooktop/oven? |  | Type | Main Energy Source | Assumed Size | Default Voltage | Default Power (VA) | Use Default? | Manual Voltage | Manual Amperage | Volt-Amps (VA) | Type | Fuel Source | Volt-Amps (VA)
Y | N | Range (cooktop and oven) | 120V Ind. CT/Oven | Electric - Induction |  |  |  | Y |  |  |  | 30" CT/Oven | Electric - Induction | 4800
N |  | Oven (seperates) - Single
N |  | Oven (seperates) - Double
N |  | Cooktop (seperates)
Carries over from Systems and Loads -> Upgrades if not upgraded
If you are adding or have an EV charger,
consider reducing the charging speed to 32 Amps or lower…
Being Upgraded? | Reduce EV Charger Speed? |  | Type | Main Energy Source | Assumed Size | Default Voltage | Default Power (VA) | Use Default? | Manual Voltage | Manual Amperage | Volt-Amps (VA) | Type | Fuel Source | Volt-Amps (VA)
Y | N | EV Charger | 16 Amp (120V) | Electric |  |  |  | Y |  |  |  | 50 Amp | Electric | 12000
Carries over from Systems and Loads -> Upgrades if not upgraded
25
A 120-Volt Heat Pump water heater will have a much smaller demand on the electrical panel, but it will come at the expense of increased recovery time for the hot water in the tank after the hot water has been depleted. This approach is viable in situations where the water heater is not serving a large number of occupants.
A Heat Pump dryer will have a smaller demand on the electrical panel, but it will come at the expense of increased dry times for a load and the dryers aren't as large as the largest traditional dryers. They mostly have the benefit of not requiring an external vent exhaust, but they also do require either being connected to a drain or to have a water pan emptied after every other load. They do require more maintenance.
A 120V appliance will use substantially less energy than 240V but is liminted in size and speed because of this.
A combined unit will save the space of a second appliance, which is beneficial in smaller dwellings.
A combined unit will normally use less energy than seperate units.
An induction stovetop/oven will use less energy than a resistance or infrared appliance, so this is a more energy efficient solution and has improved cooking speed and control that is comparable to natural gas.
A 120V induction cooktop/stove that includes a battery is a very energy efficient device that may avoid the need for pulling a 240V circuit and will have the lowest power demands of all of these kitchen devices.
A slower EV charging station will take more time to charge the car, but most people don't need full charges every night and many people will only charge on the weekends or late at night when the electric rates are lower.
Many people can sufficiently use a Level 1 charger (that plugs into a 120v wall outlet) for short commute duty, but a Level 2 charger is needed when commutes are longer or the available time to charge is short.

## Opt. 2 - Right-Size HVAC
Proposed Building Systems Changes Round #2 - HVAC Sizing Adjustments
Consider making improvements to home envelope
Being Upgraded? | Modify by changing HVAC Sizing? | Description | Type | Main Energy Source | Adjusted Size | Default Voltage | Default Power (VA) | Use Default? | Manual Voltage | Manual Amperage | Volt-Amps (VA) | Type | Fuel Source | Volt-Amps (VA)
Y | N | Space Heating | Central forced air | Electric - Heat Pump |  |  |  | Y |  |  |  | Central forced air | Electric - Heat Pump | 5760
Y | N | Air Conditioning | Central forced air | Electric |  |  |  | Y
Y | N | Ventilation | Air Handler | Electric |  |  |  | Y |  |  |  | Air Handler | Electric | 500
Consider removing the Strip Heat Backup
Being Upgraded or added? | Reduce or eliminate Strip Heat?
Y | N | Backup Strip Heat | None | Electric |  |  |  | Y |  |  |  | Strip Heat | Electric | 7200
Envelope improvements includes replacing windows and doors, replacing the dustwork with better R-value insulation, adding more insulation to the attic space, weathersealing, and other measures that will possibly reduce the need for the existing size of heating and/or cooling systems in the home. Many homes can benefit from some improvement to these, but it is not necessary to complete a home electrification.
One benefit of making these improvements is that the 'size' of the HVAC equipment can often be reduced because the improved enveloper performance will reduce heat gain/loss. This may lower the total cost of the new HVAC equipment and may benefit the electrical panel loading requirements.
Since the HVAC equipment has a 1.0 value for conincident factor, reducing the electrical demands of this equipment can have a direct benefit on the power demands in the panel calculation.
This adjustment is especially possible if the existing AC unit were oversized for the house, which is common practice and should be avoided.
The adjustment calculated assumes envelope improvements, including increased attic insulation, better performing windows and doors, and improved weatherstripping, and represents a possible reduction that could occur. More agressive changes may be possible with careful analysis by a design professional. Ensure that proper load calculations are performed by a trained design professional to ensure appropriate Heat Pump sizing chages are selected.
The calculations still must fit into typical 1/2 Ton size increments of modern Heat Pumps, so in some cases, the changes may not result in a reduction in the sizing of the unit. However, a design professional can make more detailed Schedule J calculations and determine if there is room for better improvements. These changes can be input manually.
Electric Strip Heat is commonly included in a Heat Pump system when purchased, but this is not often needed in almost all climate zones in California. This strip heat is included in the air handling unit and is commonly specified as part of that device, which in a split system is specified seperately from the condensing unit.
Strip heat has two purposes; as a backup for very cold temperatures where the HP doesn't function as well (except in high alpine areas, this does not occur in CA), and to provide heat for condensing coil defrost cycles. Defrost cycles are not needed as well in most areas unless there is high humidity and low temperatures that would cause condensation on the coils.
The strip heater backup is a very large load and in most places in California, completely unnecessary. To reduce demand for a larger panel, this will be more beneficial than added insulation and other envelope measures, but it has only a small benefit on energy consumption.
In situations where backup strip heat is required, it is possible to reduce the amount to support defrost but not function as a complete backup to the heat pump.

## Opt. 3 - Load Mgmt
Proposed Building Systems Changes Round #3 - Load Management
The following strategies can only be viably be done independent of the other approaches on this page.
For that reason, select only one of them to employ to run the calculations. The other two can be set up and the information will not be lost,
but only the option selected in the below three options will be used for the calculations.
|  | Use This Approach? |  |  | Current Setting Results
EV Charger circuit sharing |  | N | To run an option, select Y in one of the three boxes |  | 173.7167 | This approach with the current settings WILL NOT meet the original 100 amp target.
Dynamic EV charging |  | N |  |  | 173.7167 | This approach with the current settings WILL NOT meet the original 100 amp target.
Smart Panel or Smart Breakers |  | N |  |  | 173.7167 | This approach with the current settings WILL NOT meet the original 100 amp target.
Consider sharing an EV Charger and another circuit…
Exists in Home? |  | Share Circuits? |  | Choose Low Power Appliance or Initial Upgrade Values |  |  | Volt-Amps (VA) | Type | Fuel Source | Volt-Amps (VA)
N |  | N | EV Charger | Low Power Appliances |  |  | 12000 | 50 Amp | Electric | 12000
Y |  |  | Clothes Dryer | Init. Upgrade |  |  | 4000 | Side by Side Full size | Electric - Heat Pump | 4000
| Calculation results: | 173.7167 | This approach with the current settings WILL NOT meet the original 100 amp target.
Consider installing Dynamic EV charging capabilities…
Exists in Home? | Included in Electrified Home? | Dynamic charging capable? |  | Choose Low Power Appliance or Initial Upgrade Values |  |  |  | Type | Fuel Source | Volt-Amps (VA)
N | Y | N | EV Charger | Low Power Appliances |  |  |  | 50 Amp | Electric | 12000
| Calculation results: | 173.7167 | This approach with the current settings WILL NOT meet the original 100 amp target.
Consider Smart Panel or Smart Breaker devices…
Load Calculation Values
Exists in Home? | Included in Electrified Home? | Shed loads by Smart Breaker/Panel? | Description | Choose Initial Upgrade, Low Power Appliance Option, or HVAC Right-Size Source Values |  |  |  | Type | Fuel Source | Volt-Amps (VA)
Y | Y | No | Space Heating | HVAC Right-Size | Not recommended for peak shaving |  |  | Central forced air | Electric - Heat Pump | 5760
Y | Y |  | Air Conditioning |  | Not recommended for peak shaving
Y | Y |  | Ventilation |  | Not recommended for peak shaving |  |  | Air Handler | Electric | 500
N | Y |  | Strip Heat Backup |  | Not recommended for peak shaving |  |  | Strip Heat | Electric | 7200
Y | Y | No | Clothes Washer | Low Power Appliances |  |  |  | Side by Side Full size | Electric | 480
Y | Y | No | Clothes Dryer |  |  |  |  | Side by Side Full size | Electric - Heat Pump | 4000
Y | Y | No | Range (cooktop and oven) | Low Power Appliances | Not recommended for peak shaving |  |  | 30" CT/Oven | Electric - Induction | 4800
N | N | No | Oven (seperates) - Single |  | Not recommended for peak shaving
N | N | No | Oven (seperates) - Double |  | Not recommended for peak shaving
N | N | No | Cooktop (seperates) |  | Not recommended for peak shaving
Y | Y | No | Water Heater | Low Power Appliances |  |  |  | Tank < 50gal | Electric - Heat Pump | 4500
N | N | No | Water Heater 2 | Low Power Appliances
N | Y | No | EV Charger | Low Power Appliances |  |  |  | 50 Amp | Electric | 12000
N | N | No | Other Large Loads 1
N | N | No | Other Large Loads 2
N | N | No | Other Large Loads 3
Req'd | Y | No | Lighting Circuits |  | Not recommended for peak shaving |  |  |  |  | 4500
Req'd | Y | No | Small Appliance Circuits (2 circuits minimum) |  | Not recommended for peak shaving |  |  |  |  | 3000
Req'd | Y | No | Laundry Circuit (1500 VA minimum) | [6 empty] | 1500
Y | Y | No | Refrigerator |  | Not recommended for peak shaving |  |  |  |  | 750
Y | Y | No | Garbage Disposal |  | Not recommended for peak shaving |  |  |  |  | 600
Y | Y | No | Dishwasher |  | Not recommended for peak shaving |  |  |  |  | 1200
Y | Y | No | Microwave |  | Not recommended for peak shaving |  |  |  |  | 1500
Y | Y | No | Kitchen Hood |  | Not recommended for peak shaving |  |  |  |  | 250
Y | Y | No | Bathroom Fan |  | Not recommended for peak shaving |  |  |  |  | 300
N | N | No | Other Appliance 1
N | N | No | Other Appliance 2
N | N | No | Other Appliance 3
| Calculation results: | 173.7167 | This approach with the current settings WILL NOT meet the original 100 amp target.
This is an effective approach when you have two loads that are similar is size and can be schedulled so that they are not needed at the same time. For example, charge the EV after midnight and until 8AM and only run the dryer during the morning and into the evening but not late at night.
Care must be taken to ensure that there is no possible need for both at the same time or that the load schedules don't need to change often because a simple circuit sharing device cannot easily be rescheduled and it is impossible to operate both at the same time.
In most cases, the EV charger is expected to be the larger load and will determine the size of the circuit sharing device. It is also considered a continuous load and has a higher coincidence factor (CF) so it controls in these circumstances.
Because of the circuit sharing, there is less pressure to reduce the individual loads of the two appliances, but the energy efficiency improvement of a Heat Pump dryer is beneficial to consider even when circuit sharing. The default assumption is that these devices revert back to the operating parameters of the 'Electrification Goals' tab and do not use the respective values in the 'Load Reduction Options #1' tab.
This approach effectively eliminates the EV charger load during high power consumption periods and ramps it up during lower power consumption periods.
This is likely the most effective approach to reducing the potentially largest electrical load addition on the panel; the EV charger. This approach has the benefit of not requiring any change in behavior in other building systems (dryer, most commonly) and allows the EV charger to dynamically respond with different speed charging based on available power on the panel.
The lone drawback to this approach is that the estimated time to charge will not be as reliable because the charging rate will vary at times. Not all EV chargers are capable of this, so an upgrade to the EV charger may be required, and additional current monitoring equipment will be needed to interface with the EV charger to manage the charging speed.
Installing a smart panel is an effective way to manage all the loads in the house so that some can be trimmed during high power consumption periods. This approach will effectively eliminate the need for increasing the service rating, but the panel needs to be replaced completly with the new smart panel to do so. This solution is also more expensive and may be overkill for many customers because it offers control and flexability that isn't needed in most homes.
The smart panel may be a very good choice if the customer has or intends to install solar and intends to also install a battery backup system to manage the loads and charging most effectively. The smart panel can manage the battery charging (and EV charging as well) so that while there is excess solar production, the batteries are optimally charged up and when solar produciton decreases, the charging also decreases to keep the overall grid power consumption to a minimum.
A smart panel has few downsides because it is a very robust solution to the problem of power consumption management, however, there are some to consider. It is the most expensive solution. It is possibly an overkill solution for a problem that may be solved more simply and cheaply through other methods. It also is likely to be less reliable that the traditional electrical panels since it involves many more parts and added electronics to manage the loads. It also does require re-wiring the main electrical panel, so even if it avoids the need for increasing the service to the residence, it will involve utiltiy disconnection and then reconnection.

## Panel Load - Baseline (hidden)
Existing (Baseline) Panel NEC Load Calculation Report
| Panel Name | Main Panel
| Panel Voltage Rating | 240/120 V
| Main Panel Disconnect Rating | 100
General Loads
| Device | Load Description |  | Total Calculated Power (VA) | Fixed Values | Variable Values
Baseline loads | Lighting (3VA/sf) |  |  | 4500 | 4500
| Small Appliance Circuits (1500 VA per circuit) |  |  | 3000 | 3000
| Laundry Circuit (1500 VA minimum) |  |  | 1500 | 1500
Laundry
| Washer |  |  | 480 |  | 480
| Dryer |  |  | 480 |  | 480
Kitchen
| Range (oven and cooktop) |  |  | 480 |  | 480
Oven (as seperates) (single wall)
Oven (as seperates) (double wall)
Cooktop (as seperates)
| Refrigerator |  |  | 750 | 750
| Garbage Disposal |  |  | 600 | 600
| Dishwasher |  |  | 1200 | 1200
| Microwave |  |  | 1500 | 1500
| Kitchen Hood |  |  | 250 | 250
| Bathroom Fan |  |  | 300 | 300
Other Fixed Appliances
Other Appliance 1
Other Appliance 2
Other Appliance 3
Other Large Loads
Other 1
Other 2
Other 3
Water Heating
| Water heater |  |  | 305 |  | 305
Water Heater 2
HVAC
| Space Heating | Not counted in 40% calc | 100 | 5700
| Air Conditioning | Not counted in 40% calc | 5100
| Ventilation | Not counted in 40% calc | 600
| Strip Heat (65% CF applied) | Not counted in 40% calc | 0
EV Charger
| EV Charger | Not counted in 40% calc |  | 0 |  | 0
Service Load Volt-Amperes (VA) |  |  |  | 15345 | 13600 | 1745
Initial 8,000 VA |  |  |  | 8000 | 8000
40% Coincidence Factor over 8,000 (VA) |  |  |  | 2938 | 2240 | 698
HVAC |  |  | (1.0 CF) | 5700 |  | 5700
EV Charger |  |  | (1.25 CF) | 0 |  | 0
Total VA |  |  |  | 16638 | 10240 | 6398
Total Service Load Amperes (A) |  |  |  | 69.325 | 42.6667 | 26.6583
Service Rating Amperes (A) |  |  |  | 100
The calculations for HVAC and EV charger apply 1.0 and 1.25 coincidence factors. This is a conservative position for an existing conditions calculation based on NEC 220.83(A), where the code is somewhat vague but it appears these could be included in the 40% calc. However, since the existing HVAC (and presumably EV charger) could be getting upgraded and/or electrified, there will be increased load, so the new loads will be treated with these factors per NEC 220.83(B) and 625.14 and it seems fair that if there is existing loads in these categories, they be calculated with them as well.
The EV Charger 1.25 CF factor comes from 625.14 as a continuous load.

## Panel Load - Goal (hidden)
Hidden Tab
Existing (Baseline) Panel NEC Load Calculation Report
|  | Panel Name | Main Panel
|  | Panel Voltage Rating | 240/120 V
|  | Main Panel Disconnect Rating | 100
General Loads
|  | Device | Load Description |  | Total Calculated Power (VA)
| Baseline loads | Lighting (3VA/sf) |  |  | 4500 | 4500
|  | Small Appliance Circuits (1500 VA per circuit) |  |  | 3000 | 3000
|  | Laundry Circuit (1500 VA minimum) |  |  | 1500 | 1500
Laundry
|  | Washer |  |  | 480 |  | 480
|  | Dryer |  |  | 4000 |  | 4000
Kitchen
|  | Range (oven and cooktop) |  |  | 4800 |  | 4800
Oven (as seperates) (single wall)
Oven (as seperates) (double wall)
Cooktop (as seperates)
|  | Refrigerator |  |  | 750 | 750
|  | Garbage Disposal |  |  | 600 | 600
|  | Dishwasher |  |  | 1200 | 1200
|  | Microwave |  |  | 1500 | 1500
|  | Kitchen Hood |  |  | 250 | 250
|  | Bathroom Fan |  |  | 300 | 300
Other Fixed Appliances
Other Appliance 1
Other Appliance 2
Other Appliance 3
Other Large Loads
Other 1
Other 2
Other 3
Water Heating
|  | Water heater |  |  | 4500 |  | 4500
Water Heater 2
HVAC
|  | Space Heating | Not counted in 40% calc | 5760 | 10940
|  | Air Conditioning | Not counted in 40% calc
|  | Ventilation | Not counted in 40% calc | 500
|  | Strip Heat (65% CF applied) | Not counted in 40% calc | 4680
EV Charger
|  | EV Charger | Not counted in 40% calc |  | 12000
| Service Load Volt-Amperes (VA) |  |  |  | 27380 | 13600 | 13780
| Initial 8,000 VA |  |  |  | 8000 | 8000
| 40% Coincidence Factor over 8,000 (VA) |  |  |  | 7752 | 2240 | 5512
| HVAC |  |  | (1.0 CF) | 10940 |  | 10940
| EV Charger |  |  | (1.25 CF) | 15000 |  | 15000
| Total VA |  |  |  | 41692 | 10240 | 31452
| Total Service Load Amperes (A) |  |  |  | 173.7167 | 42.6667 | 131.05
| Service Rating Amperes (A) |  |  |  | 100

## Panel Load - Opt1 (hidden)
Hidden Tab
Opt1 Panel NEC Load Calculation Report
|  | Panel Name | Main Panel
|  | Panel Voltage Rating | 240/120 V
|  | Main Panel Disconnect Rating | 100
General Loads
|  | Device | Load Description |  | Total Calculated Power (VA)
| Baseline loads | Lighting (3VA/sf) |  |  | 4500 | 4500
|  | Small Appliance Circuits (1500 VA per circuit) |  |  | 3000 | 3000
|  | Laundry Circuit (1500 VA minimum) |  |  | 1500 | 1500
Laundry
|  | Washer |  |  | 480 |  | 480
|  | Dryer |  |  | 4000 |  | 4000
Kitchen
|  | Range (oven and cooktop) |  |  | 4800 |  | 4800
Oven (as seperates) (single wall)
Oven (as seperates) (double wall)
Cooktop (as seperates)
|  | Refrigerator |  |  | 750 | 750
|  | Garbage Disposal |  |  | 600 | 600
|  | Dishwasher |  |  | 1200 | 1200
|  | Microwave |  |  | 1500 | 1500
|  | Kitchen Hood |  |  | 250 | 250
|  | Bathroom Fan |  |  | 300 | 300
Other Fixed Appliances
Other Appliance 1
Other Appliance 2
Other Appliance 3
Other Large Loads
Other 1
Other 2
Other 3
Water Heating
|  | Water heater |  |  | 4500 |  | 4500
Water Heater 2
HVAC
|  | Space Heating | Not counted in 40% calc | 5760 | 10940
|  | Air Conditioning | Not counted in 40% calc
|  | Ventilation | Not counted in 40% calc | 500
|  | Strip Heat (65% CF applied) | Not counted in 40% calc | 4680
EV Charger
|  | EV Charger | Not counted in 40% calc |  | 12000
| Service Load Volt-Amperes (VA) |  |  |  | 27380 | 13600 | 13780
| Initial 8,000 VA |  |  |  | 8000 | 8000
| 40% Coincidence Factor over 8,000 (VA) |  |  |  | 7752 | 2240 | 5512
| HVAC |  |  | (1.0 CF) | 10940 |  | 10940
| EV Charger |  |  | (1.25 CF) | 15000 |  | 15000
| Total VA |  |  |  | 41692 | 10240 | 31452
| Total Service Load Amperes (A) |  |  |  | 173.7167 | 42.6667 | 131.05
| Service Rating Amperes (A) |  |  |  | 100

## Panel Load - Opt2 (hidden)
Hidden Tab
Opt2 Panel NEC Load Calculation Report - HVAC Resizing
|  | Panel Name | Main Panel
|  | Panel Voltage Rating | 240/120 V
|  | Main Panel Disconnect Rating | 100
General Loads
|  | Device | Load Description |  | Total Calculated Power (VA)
| Baseline loads | Lighting (3VA/sf) |  |  | 4500 | 4500
|  | Small Appliance Circuits (1500 VA per circuit) |  |  | 3000 | 3000
|  | Laundry Circuit (1500 VA minimum) |  |  | 1500 | 1500
Laundry
|  | Washer |  |  | 480 |  | 480
|  | Dryer |  |  | 4000 |  | 4000
Kitchen
|  | Range (oven and cooktop) |  |  | 4800 |  | 4800
Oven (as seperates) (single wall)
Oven (as seperates) (double wall)
Cooktop (as seperates)
|  | Refrigerator |  |  | 750 | 750
|  | Garbage Disposal |  |  | 600 | 600
|  | Dishwasher |  |  | 1200 | 1200
|  | Microwave |  |  | 1500 | 1500
|  | Kitchen Hood |  |  | 250 | 250
|  | Bathroom Fan |  |  | 300 | 300
Other Fixed Appliances
Other Appliance 1
Other Appliance 2
Other Appliance 3
Other Large Loads
Other 1
Other 2
Other 3
Water Heating
|  | Water heater |  |  | 4500 |  | 4500
Water Heater 2
HVAC
|  | Space Heating | Not counted in 40% calc | 5760 | 10940
|  | Air Conditioning | Not counted in 40% calc | 0
|  | Ventilation | Not counted in 40% calc | 500
|  | Strip Heat (65% CF applied) | Not counted in 40% calc | 4680
EV Charger
|  | EV Charger | Not counted in 40% calc |  | 12000
| Service Load Volt-Amperes (VA) |  |  |  | 27380 | 13600 | 13780
| Initial 8,000 VA |  |  |  | 8000 | 8000
| 40% Coincidence Factor over 8,000 (VA) |  |  |  | 7752 | 2240 | 5512
| HVAC |  |  | (1.0 CF) | 10940 |  | 10940
| EV Charger |  |  | (1.25 CF) | 15000 |  | 15000
| Total VA |  |  |  | 41692 | 10240 | 31452
| Total Service Load Amperes (A) |  |  |  | 173.7167 | 42.6667 | 131.05
| Service Rating Amperes (A) |  |  |  | 100

## Panel Load - Opt3a (hidden)
Hidden Tab
Opt3a Panel NEC Load Calculation Report - Circuit Sharing
|  | Panel Name | Main Panel
|  | Panel Voltage Rating | 240/120 V
|  | Main Panel Disconnect Rating | 100
General Loads
|  | Device | Load Description |  | Total Calculated Power (VA)
| Baseline loads | Lighting (3VA/sf) |  |  | 4500 | 4500
|  | Small Appliance Circuits (1500 VA per circuit) |  |  | 3000 | 3000
|  | Laundry Circuit (1500 VA minimum) |  |  | 1500 | 1500
Laundry
|  | Washer |  |  | 480 |  | 480
|  | Dryer | Dryer removed because shared with EV charger |  | 4000 |  | 4000
Kitchen
|  | Range (oven and cooktop) |  |  | 4800 |  | 4800
Oven (as seperates) (single wall)
Oven (as seperates) (double wall)
Cooktop (as seperates)
|  | Refrigerator |  |  | 750 | 750
|  | Garbage Disposal |  |  | 600 | 600
|  | Dishwasher |  |  | 1200 | 1200
|  | Microwave |  |  | 1500 | 1500
|  | Kitchen Hood |  |  | 250 | 250
|  | Bathroom Fan |  |  | 300 | 300
Other Fixed Appliances
Other Appliance 1
Other Appliance 2
Other Appliance 3
Other Large Loads
Other 1
Other 2
Other 3
Water Heating
|  | Water heater |  |  | 4500 |  | 4500
Water Heater 2
HVAC
|  | Space Heating | Not counted in 40% calc | 5760 | 10940
|  | Air Conditioning | Not counted in 40% calc | 0
|  | Ventilation | Not counted in 40% calc | 500
|  | Strip Heat (65% CF applied) | Not counted in 40% calc | 4680
EV Charger
|  | EV Charger | Not counted in 40% calc |  | 12000
| Service Load Volt-Amperes (VA) |  |  |  | 27380 | 13600 | 13780
| Initial 8,000 VA |  |  |  | 8000 | 8000
| 40% Coincidence Factor over 8,000 (VA) |  |  |  | 7752 | 2240 | 5512
| HVAC |  |  | (1.0 CF) | 10940 |  | 10940
| EV Charger |  |  | (1.25 CF) | 15000 |  | 15000
| Total VA |  |  |  | 41692 | 10240 | 31452
| Total Service Load Amperes (A) |  |  |  | 173.7167 | 42.6667 | 131.05
| Service Rating Amperes (A) |  |  |  | 100

## Panel Load - Opt3b (hidden)
Hidden Tab
Opt3b Panel NEC Load Calculation Report - Dynamic EV Charging
|  | Panel Name | Main Panel
|  | Panel Voltage Rating | 240/120 V
|  | Main Panel Disconnect Rating | 100
General Loads
|  | Device | Load Description |  | Total Calculated Power (VA)
| Baseline loads | Lighting (3VA/sf) |  |  | 4500 | 4500
|  | Small Appliance Circuits (1500 VA per circuit) |  |  | 3000 | 3000
|  | Laundry Circuit (1500 VA minimum) |  |  | 1500 | 1500
Laundry
|  | Washer |  |  | 480 |  | 480
|  | Dryer |  |  | 4000 |  | 4000
Kitchen
|  | Range (oven and cooktop) |  |  | 4800 |  | 4800
Oven (as seperates) (single wall)
Oven (as seperates) (double wall)
Cooktop (as seperates)
|  | Refrigerator |  |  | 750 | 750
|  | Garbage Disposal |  |  | 600 | 600
|  | Dishwasher |  |  | 1200 | 1200
|  | Microwave |  |  | 1500 | 1500
|  | Kitchen Hood |  |  | 250 | 250
|  | Bathroom Fan |  |  | 300 | 300
Other Fixed Appliances
Other Appliance 1
Other Appliance 2
Other Appliance 3
Other Large Loads
Other 1
Other 2
Other 3
Water Heating
|  | Water heater |  |  | 4500 |  | 4500
Water Heater 2
HVAC
|  | Space Heating | Not counted in 40% calc | 5760 | 10940
|  | Air Conditioning | Not counted in 40% calc | 0
|  | Ventilation | Not counted in 40% calc | 500
|  | Strip Heat (65% CF applied) | Not counted in 40% calc | 4680
EV Charger
|  | EV Charger | Not counted in 40% calc |  | 12000
| Service Load Volt-Amperes (VA) |  |  |  | 27380 | 13600 | 13780
| Initial 8,000 VA |  |  |  | 8000 | 8000
| 40% Coincidence Factor over 8,000 (VA) |  |  |  | 7752 | 2240 | 5512
| HVAC |  |  | (1.0 CF) | 10940 |  | 10940
| EV Charger |  |  | (1.25 CF) | 15000 |  | 15000
| Total VA |  |  |  | 41692 | 10240 | 31452
| Total Service Load Amperes (A) |  |  |  | 173.7167 | 42.6667 | 131.05
| Service Rating Amperes (A) |  |  |  | 100

## Panel Load - Opt3c (hidden)
Hidden Tab
Opt3c Panel NEC Load Calculation Report - Dynamic EV Charging
|  | Panel Name | Main Panel
|  | Panel Voltage Rating | 240/120 V
|  | Main Panel Disconnect Rating | 100
General Loads
|  | Device | Load Description |  | Total Calculated Power (VA)
| Baseline loads | Lighting (3VA/sf) |  |  | 4500 | 4500
|  | Small Appliance Circuits (1500 VA per circuit) |  |  | 3000 | 3000
|  | Laundry Circuit (1500 VA minimum) |  |  | 1500 | 1500
Laundry
|  | Washer |  |  | 480 |  | 480
|  | Dryer |  |  | 4000 |  | 4000
Kitchen
|  | Range (oven and cooktop) |  |  | 4800 |  | 4800
Oven (as seperates) (single wall)
Oven (as seperates) (double wall)
Cooktop (as seperates)
|  | Refrigerator |  |  | 750 | 750
|  | Garbage Disposal |  |  | 600 | 600
|  | Dishwasher |  |  | 1200 | 1200
|  | Microwave |  |  | 1500 | 1500
|  | Kitchen Hood |  |  | 250 | 250
|  | Bathroom Fan |  |  | 300 | 300
Other Fixed Appliances
Other Appliance 1
Other Appliance 2
Other Appliance 3
Other Large Loads
Other 1
Other 2
Other 3
Water Heating
|  | Water heater |  |  | 4500 |  | 4500
Water Heater 2
HVAC
|  | Space Heating | Not counted in 40% calc | 5760 | 10940
|  | Air Conditioning | Not counted in 40% calc | 0
|  | Ventilation | Not counted in 40% calc | 500
|  | Strip Heat (65% CF applied) | Not counted in 40% calc | 4680
EV Charger
|  | EV Charger | Not counted in 40% calc |  | 12000
| Service Load Volt-Amperes (VA) |  |  |  | 27380 | 13600 | 13780
| Initial 8,000 VA |  |  |  | 8000 | 8000
| 40% Coincidence Factor over 8,000 (VA) |  |  |  | 7752 | 2240 | 5512
| HVAC |  |  | (1.0 CF) | 10940 |  | 10940
| EV Charger |  |  | (1.25 CF) | 15000 |  | 15000
| Total VA |  |  |  | 41692 | 10240 | 31452
| Total Service Load Amperes (A) |  |  |  | 173.7167 | 42.6667 | 131.05
| Service Rating Amperes (A) |  |  |  | 100

## Reference (hidden)
Property Information
Type of Residence | Year of Construction | Utility
Detached SF | Before - 1975 | PG&E
Duplex | 1976 - 2000 | SCE
Triplex | 2000 or Newer | SDG&E
PacifiCorp
Liberty
Local POU
Baseline Systems
Include? | Laundry Circuits | Small Appliance Circuits | Panel Voltage Rating
Y | 0 | 2 | 240 - 120 V
N | 1 | 3 | 120 V
| 2 | 4
| 3 | 5
4
|  | Tons | [7 empty] | BTU/sf | W/ton
Space Heating Types | Space Heating Energy Source | Heating size | Default Electrical NG/P/FO | Electric Resistance | Heat Pump Nameplate |  |  | Air Conditioning Type |  | Air Conditioning Size | AC Nameplate |  |  | Ventilation | Ventilation Default | Strip Heater | Strip Heat Default
Central forced air | NG, Propane, Fuel oil | 3 | 100 | 9600 | 5760 |  |  | Central forced air |  | 14.058 | 2750 |  |  | Air Handler | 600 | Strip Heat | 7200
Baseboard | Electric Resistance | [6 empty] | Window Unit/s | [5 empty] | None | 0 | None | 0
Other | Electric - Heat Pump | [6 empty] | Swamp Cooler / Whole House Fan |  |  | 750
|  |  | Assume 100w for a pump or blower and electronics | Convert btu/h of heating size to W | [6 empty] | Assume 11 SEER, about 1100 watts per ton | [5 empty] | Assumes 75% of heat load is used for strip heat backup.
Clothes Washer Type | Default Clothes Washer | Clothes Dryer Type | Clothes Dryer Energy Source | Clothes Dryer Size | Default NG Dryer |  | Default Elec Dryer | Default HP Dryer
Side by Side Full size | 480 | Side by Side Full size | NG, Propane |  | 480 |  | 5760 | 5760
Combination Wash/Dry |  | Combination Wash/Dry | Electric Resistance
Stacked Wash/Dry |  | Stacked Wash/Dry | Electric - Heat Pump
Combined Range |  |  |  |  | Separate Oven Single | [5 empty] | Separate Oven Double |  |  |  |  | Separate Cooktop
Stove Type | Stove Energy Source | Default NG Combo | Default Elec Combo | Default IND Combo | Oven Type |  | Energy Source | Default NG Oven Single |  | Default Elec Oven Single | Oven Type | Energy Source |  | Default NG Oven Double | Default Elec Oven Double | CT Type | Energy Source | Default NG CT | Default Elec CT | Default IND CT
24" (Apt. sz.) CT/Oven | NG, Propane | 480 | 4800 | 4800 | 30" Single Oven |  | NG, Propane | 480 |  | 4800 | 30" Double Oven | NG, Propane |  | 480 | 8000 | 30" Cooktop | NG, Propane | 480 | 3600 | 3600
30" CT/Oven | Electric Resistance | [5 empty] | Electric Resistance |  |  |  |  | Electric Resistance |  |  |  | 36" Cooktop | Electric Resistance
36" CT/Oven | Electric - Induction | [15 empty] | Electric - Induction
Water Heater Type | Water Heater Energy Source | Tankless NG Default | WH NG Default | WH Elec Tankless Default | WH Elec Default |  | WH HP Default
Tankless 3gpm | NG, Propane | 300 | 305 | 20000
Tankless 5gpm | Electric Resistance |  |  | 26400
Tank < 50gal | Electric - Heat Pump |  |  |  | 5000 |  | 4500
Tank >= 50gal |  |  |  |  | 5500 |  | 5000
EV Charger | EV Wattage
32 Amp | 7680
40 Amp | 9600
50 Amp | 12000
Panel Loads
Use NEC Defaults (Y Default) | Voltage | Panel Load Rating
Y | 120 | 80
N | 240 | 100
125
150
200
225
400
Energy Source
Electric
NG/Propane
Other
|  |  |  | Data pulled from Baseline calcs file | [7 empty] | btu/h per SF |  | Total | Total | Total
County List | CZ Assignment | CZ CALC Sub |  | CZ3 | [6 empty] | Date Match | Heating Formula |  | Heat Sizing (Ton) | Electric Res. Heat | Electric Res. Heat Size | HP Elect Nameplate
Alameda | 3 | 3 |  |  | Heat |  |  | Cool |  |  | 1 | 18.4723 |  | 3 | 8118.5691 | 9600 | 5760
Alpine | 16 | 16 |  |  | =x2 | =x | constant | =x2 | =x | constant | [5 empty] | … up to the nearest 10-amp 240 breaker
Amador | 12 | 12 |  | 1960 | 2.03e-06 | -0.0117 | 27.303 | 2.43e-06 | -0.0127 | 23.73 |  | btu/h per SF |  | Total
Butte | 11 | 16 |  | 1985 | 1.58e-06 | -0.0088 | 20.279 | 2.3e-06 | -0.01189 | 21.49 | County Match | Cooling Formula |  | Cool Sizing (Ton) |  | AC Elect Nameplate OLDER UNIT |  | AC Elect Nameplate NEW UNIT
Calaveras | 12 | 12 |  | 2005 | 1.34e-06 | -0.007534 | 17.402 | 2.19e-06 | -0.01125 | 19.837 | 8 | 14.058 |  | 2.5 |  | 5100 |  | 4350
Colusa | 11 | 16 |  | CZ9 | [6 empty] | These adjust the location on the table to the left to get the correct formula.
Contra Costa | 3 | 3 |  | 1960 | 2.22e-06 | -0.012809 | 30.0172 | 2.74e-06 | -0.01466 | 27.8131 | These are a translation of the cnty and date to array row adjustments!
Del Norte | 1 | 3 |  | 1985 | 1.73e-06 | -0.009679 | 22.3124 | 2.46e-06 | -0.012831 | 23.3149
El Dorado | 12 | 12 |  | 2005 | 1.48e-06 | -0.0082916 | 19.173 | 2.37e-06 | -0.012128 | 21.1832 |  | RESIZE FOR ENVELOPE
Fresno | 13 | 12 |  | CZ12 | [7 empty] | btu/h per SF |  | Total | Total | Total
Glenn | 16 | 16 |  | 1960 | 2.61e-06 | -0.015003 | 35.1038 | 2.93e-06 | -0.016001 | 31.4672 |  | Heating Formula |  | Heat Sizing (Ton) | Electric Res. Heat | Electric Res. Heat Size | HP Elect Nameplate
Humboldt | 1 | 3 |  | 1985 | 2.03e-06 | -0.011321 | 26.0675 | 2.59e-06 | -0.013776 | 25.8881 |  | 13.6535 |  | 2 | 6000.7098 | 7680 | 3840
Imperial | 15 | 9 |  | 2005 | 1.73e-06 | -0.0096811 | 22.3691 | 2.4e-06 | -0.012651 | 23.1661 | [5 empty] | … up to the nearest 10-amp 240 breaker
Inyo | 16 | 16 |  | CZ16
Kern | 13 | 12 |  | 1960 | 3.15e-06 | -0.018268 | 43.1231 | 2.31e-06 | -0.01216 | 22.8299 |  | btu/h per SF |  | Total
Kings | 13 | 12 |  | 1985 | 2.47e-06 | -0.013884 | 32.1965 | 2.22e-06 | -0.011526 | 20.8638 |  | Cooling Formula |  | Cool Sizing (Ton) |  |  | AC Elect Nameplate
Lake | 2 | 3 |  | 2005 | 2.13e-06 | -0.012003 | 27.849 | 2.15e-06 | -0.011033 | 19.4441 |  | 11.052 |  | 2 |  |  | 3480
Lassen | 16 | 16
Los Angeles | 9 | 9
Madera | 13 | 12 | [9 empty] | AC Data |  |  |  | HP Data
Marin | 3 | 3 | [9 empty] | Trane |  | 4TTR Line |  | Daikin Data | Fit Series
Mariposa | 12 | 12 | [9 empty] | 2 |  | 13.4 | 6.7 | 1.5 | 14.6 | 9.7333
Mendocino | 1 | 3 | [9 empty] | 3 |  | 18.4 | 6.1333 | 2 | 18.8 | 9.4
Merced | 12 | 12 | [9 empty] | 4 |  | 28 | 7 | 2.5 | 23.9 | 9.56
Modoc | 16 | 16 | [9 empty] | 5 |  | 35 | 7 | 3 | 23.9 | 7.9667
Mono | 16 | 16 | [13 empty] | 3.5 | 34.4 | 9.8286
Monterey | 3 | 3 | [9 empty] | Daikin |  | Fit DX6 series |  | 4 | 34.4 | 8.6
Napa | 2 | 3 | [9 empty] | 1.5 |  | 14.6 | 9.7333 | 5 | 36.2 | 7.24
Nevada | 11 | 16 | [9 empty] | 2 |  | 18.8 | 9.4
Orange | 6 | 3 | [9 empty] | 2.5 |  | 23.9 | 9.56
Placer | 11 | 16 | [9 empty] | 3 |  | 23.9 | 7.9667 | Trane Data | 4TWR70xxxxx | XR17 line
Plumas | 16 | 16 | [9 empty] | 3.5 |  | 34.4 | 9.8286 | 2 | 15 | 7.5
Riverside | 10 | 12 | [9 empty] | 4 |  | 34.4 | 8.6 | 3 | 21 | 7
Sacramento | 12 | 12 | [9 empty] | 5 |  | 36.2 | 7.24 | 4 | 28 | 7
San Bernardino | 10 | 12 | [13 empty] | 5 | 37 | 7.4
San Diego | 7 | 3 | [9 empty] | Daikin |  | DX4 series
San Francisco | 3 | 3 | [9 empty] | 1.5 |  | 11.9 | 7.9333 | Trane Data | 4TWR60xxxxx | XR16 line
San Joaquin | 12 | 12 | [9 empty] | 2 |  | 15.3 | 7.65 | 2 | 15 | 7.5
San Luis Obispo | 3 | 3 | [9 empty] | 2.5 |  | 17 | 6.8 | 3 | 22 | 7.3333
San Mateo | 3 | 3 | [9 empty] | 3 |  | 18.6 | 6.2 | 4 | 28 | 7
Santa Barbara | 5 | 3 | [9 empty] | 3.5 |  | 23.4 | 6.6857 | 5 | 41 | 8.2
Santa Clara | 4 | 3 | [9 empty] | 4 |  | 26.2 | 6.55
Santa Cruz | 3 | 3 | [9 empty] | 5 |  | 32.4 | 6.48
Shasta | 11 | 16
Sierra | 16 | 16 | [9 empty] | Goodman | GVXC20 series
Siskiyou | 16 | 16 | [9 empty] | 2 |  | 15.2 | 7.6
Solano | 12 | 12 | [9 empty] | 3 |  | 20.6 | 6.8667
Sonoma | 1 | 3 | [9 empty] | 4 |  | 30.1 | 7.525
Stanislaus | 12 | 12 | [9 empty] | 5 |  | 31.1 | 6.22
Sutter | 11 | 16
Tehama | 11 | 16 | [9 empty] | Goodman | GXSN3 series
Trinity | 2 | 3 | [9 empty] | 1.5 |  | 8.3 | 5.5333
Tulare | 13 | 12 | [9 empty] | 2 |  | 11.2 | 5.6
Tuolumne | 12 | 12 | [9 empty] | 2.5 |  | 16.1 | 6.44
Ventura | 16 | 16 | [9 empty] | 3 |  | 18.6 | 6.2
Yolo | 12 | 12 | [9 empty] | 3.5 |  | 23.1 | 6.6
Yuba | 11 | 16 | [9 empty] | 4 |  | 24.4 | 6.1
[12 empty] | 5 |  | 33.3 | 6.66

## Reference2 (hidden)
Retrofit Options Information
Retrofit
|  |  |  | W/ton |  |  |  | W/ton
Space Heating Types | Space Heating Energy Source |  |  | Upgraded Heat Pump |  | Air Conditioning Type |  | AC Efficiency |  | Ventilation | Ventilation Default | Strip Heat | Strip Heat Default | Strip Heat REDUCE | Strip Heat Default
Central forced air | Electric - Heat Pump |  |  | 2580 |  | Central forced air |  | 860 |  | Air Handler | 500 | Strip Heat | 7200 | None | 0
Baseboard | [5 empty] | Window Unit/s |  |  |  | None | 0 | None |  | Reduce Strip Heat 25% | 5400
Minisplit | [5 empty] | Minisplit | [7 empty] | Reduce Strip Heat 50% | 3600
Other | [5 empty] | None (Remove AC) | [7 empty] | Reduce Strip Heat 75% | 1800
|  |  |  | Assume 17 SEER, about 860 watts per ton |  |  |  | Assume 17 SEER, about 860 watts per ton |  |  |  |  | Assumes 75% of heat load is used for strip heat backup.
Clothes Washer Type | Clothes Washer Default | Clothes Dryer Type | Clothes Dryer Energy Source | Clothes Dryer Size | Default Elec Dryer | Default HP Dryer
Side by Side Full size | 480 | Side by Side Full size | Electric Resistance |  | 5760 | 4000
Combination Wash/Dry |  | Combination Wash/Dry | Electric - Heat Pump
Stacked Wash/Dry |  | Stacked Wash/Dry
Combined Range |  |  |  | Separate Oven Single |  |  | Separate Oven Double |  |  | Separate Cooktop
Stove Type | Stove Energy Source | Default Elec Combo | Default IND Combo | Oven Type | Energy Source | Default Elec Oven Single | Oven Type | Energy Source | Default Elec Oven Double | CT Type | Energy Source | Default Elec CT | Default IND CT
24" (Apt. sz.) CT/Oven | Electric Resistance | 4800 | 4800 | 30" Single Oven | Electric Resistance | 4800 | 30" Double Oven | Electric Resistance | 8000 | 30" Cooktop | Electric Resistance | 3600 | 3600
30" CT/Oven | Electric - Induction | [8 empty] | 36" Cooktop | Electric - Induction
36" CT/Oven
Water Heater Type | Water Heater Energy Source | WH Elec Tankless Default | WH Elec Default | WH HP Default
Tankless 3gpm | Electric Resistance | 20000
Tankless 5gpm | Electric - Heat Pump | 26400
Tank < 50gal | None |  | 5000 | 4500
Tank >= 50gal |  |  | 5500 | 5000
Delete WH
EV Charger | EV Wattage
32 Amp | 7680
40 Amp | 9600
50 Amp | 12000
Panel Loads
Use NEC Defaults (Y Default) | Use NEC Defaults (# of circuits) | Voltage
Y | 2 | 120
N | 3 | 240
4
5
6
7
8
Reduction Strategies
Shared Circuits 1 | Shared Circuits 2
EV Charger
Dryer
Range

## Reference3 (hidden)
Retrofit Options Information
Retrofit
|  | BTU/sf |  | W/sf | W/ton |  |  | BTU/sf | W/ton
Space Heating Types | Space Heating Energy Source | Heating size | HP Sizes | Default Electric Resistance | Default Heat Pump |  | Air Conditioning Type | Air Conditioning Size | AC Efficiency
Central forced air | Electric Resistance | 35 | 2 | 10 | 710 |  | Central Air | 25 | 710
Baseboard | Electric - Heat Pump |  | 2.5 |  |  |  | Window Unit/s
Minisplit |  |  | 3 |  |  |  | Minisplit
Other |  |  | 3.5 |  |  |  | None (Remove AC)
4
5
Clothes Dryer Type | Clothes Dryer Energy Source | Default HP Dryer
Side by Side dryer | Electric - Heat Pump | 4000 | Check all values |  |  | Pulled from https://www.energysage.com/electricity/house-watts/how-many-watts-does-an-air-conditioner-use/
120V Side by Side dryer |  | 1500 | Check all values
Combo Wash/Dry |  | 1500 | Check all values
Combined Range
Stove Type | Cooktop Energy Source | Default IND Combo
Induction Cooktop/Oven | Electric - Induction | 4800 | Check all values
120V Ind. CT/Oven |  | 1920 | Check all values
Water Heater Type | Water Heater Energy Source | WH 120HP Default
Tank < 50gal | Electric - HP 120V | 1440
Delete WH | None
EV Charger | EV Wattage
16 Amp (120V) | 1920
20 Amp | 4800
32 Amp | 7680
40 Amp | 9600
Source Values | Source Values 2
Low Power Appliances | HVAC Right-Size
Init. Upgrade | Init. Upgrade
Smart Panel
No
Yes

## Panel Calc Resources (hidden)
[18 empty] | Fixed Loads |  |  | Possible Impacted Loads |  |  | Free Load Capacity |  |  | Excess Load Need
| Ex Panel Rtg | New Elect. Panel Size | Opt2 | Opt3 | Fixed | Variable | Available | Over Panel Rtg. | Normalization Value | Max Amps Value | Max Panel Rating | Total Load | Total Amps | Original Panel size | Needed New Panel Size | Voltage | Total VA Available | Load | Amps | Percent of Available | Load | Amps | Percent of Available | Load | Amps | Percent of Available | Load | Amps | Percent Overage
| 100 | 200 | 200 | 200
Baseline | 100 | 200 | 200 | 200 | 42.6667 | 26.6583 | 30.675 | 0 | 0.34663 | 173.7167 | 200 | 16638 | 69.325 | 100 | 100 | 240 | 24000 | 10240 | 42.6667 | 42.67% | 6398 | 26.6583 | 26.66% | 7362 | 30.675 | 30.68% | 0 | 0 | 0%
Electrification Upgrades | 100 | 200 | 200 | 200 | 42.6667 | 57.3333 | 0 | 73.7167 | 0.86858 |  |  | 41692 | 173.7167 | 100 | 200 | 240 | 24000 | 10240 | 42.6667 | 42.67% | 31452 | 131.05 | 131.1% | 0 | 0 | 0% | 17692 | 73.7167 | 73.72%
Low Power Appliances | 100 | 200 | 200 | 200 | 42.6667 | 57.3333 | 0 | 73.7167 | 0.86858 |  |  | 41692 | 173.7167 | 100 | 200 | 240 | 24000 | 10240 | 42.6667 | 42.67% | 31452 | 131.05 | 131.1% | 0 | 0 | 0% | 17692 | 73.7167 | 73.72%
Right Size HVAC | 100 | 200 | 200 | 200 | 42.6667 | 57.3333 | 0 | 73.7167 | 0.86858 |  |  | 41692 | 173.7167 | 100 | 200 | 240 | 24000 | 10240 | 42.6667 | 42.67% | 31452 | 131.05 | 131.1% | 0 | 0 | 0% | 17692 | 73.7167 | 73.72%
No Load Mgmt Selected | 100 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0.86858 |  |  | 41692 | 173.7167 | 100 | 200 | 240 | 24000 | 10240 | 42.6667 | 42.67% | 31452 | 131.05 | 131.1% | 0 | 0 | 0% | 17692 | 73.7167 | 73.72%
| 100 | 200 | 200 | 200
Panel Status messages
The existing main electrical panel is 100 Amps.
With all the electrification measures chosen in the 'Electrification Upgrades' tab, the minimum size electrical panel and service will need to be 200 Amps.
The current optimization measures are insufficient to lower the panel size below the 200 Amp size.
Panel optimization recommendation messages
The electrification upgrades selected will require a panel and service upgrade, but follow the optimization options recommendations below to mitigate this impact.
Your current optimization selections exceed your existing panel capacity, and require an upgrade to a 200 Amp service. Consider making additional optimization selections, or proceed with a service upgrade.
Low Power Appliances - No LPA options are chosen. Go to the LPA tab and select options that are viable for the client.
Right Size HVAC - No HVAC options are chosen. Go to the HVAC tab and select options that are viable for the client if applicable through HVAC or envelope upgrades.
Load Management - No LM options are chosen. Go to the LM tab and select options that are viable for the client .
The optimized main electrical panel is 200 Amps.