## Landing Page
CalNext Craft Brewery Screening Tool
Navigation
Screen (tab) | Description
Introduction | This sheet gives an overview of the three heat pump technologies and their uses in craft breweries.
Comparison Calculations | This sheet is the main tool, strongly suggest the user begin calculations here.
Reference | This sheet includes reference values used in equations along with their sources
Data Dictionary | This sheet defines all the variables and assumptions used in the tool.
Heat Recovery | This sheet goes into detail about the inputs, outputs, and calculations for the heat recovery technology specifically.
ASHPWH | This sheet goes into detail about the inputs, outputs, and calculations for the air source heat pump water heater technology specifically.
SGHP | This sheet goes into detail about the inputs, outputs, and calculations for the steam generating heat pump technology specifically.
Other EE Measures | This sheet includes a measure list of other energy efficient measure options to consider for brewers.
What does the tool do?
The Craft Brewery Industrial Heat Pump Screening tool is intended to inform interested parties about opportunities for incorporating heat pumps into brewery operations, and heat pump performance. The tool can also help understand the viability of potential industrial heat pump installations for small and medium business craft breweries. The tool will help the decision-makers understand the benefits of heat pumps, the estimated equipment operating energy and cost impacts involved with their specific brewery operations, and other options that they might have for energy efficiency.
How is the tool used?
The tool requires the user to input water temperatures, energy use and cost, volumes, and equipment efficiency where appropriate to calculate estimated energy use, emissions, and equipment energy costs for three different heat pump technologies. Start with the "Comparison Calculations" tab. If you have questions on any variables or assumptions, visit the reference and data dictionary tabs. For detailed calculations on specific technologies, visit each of the heat recovery, air source heat pump water heater (ASHPWH) and steam generating heat pump (SGHP) tabs. For best results, view this tool using a laptop or desktop computer.
Who should use this tool?
All interested parties are encouraged to use the tool to see the benefits of heat pump technology, but the tool is primarily designed for staff at craft breweries that have a strong understanding of their breweries facilities, operations, and energy usage. This tool only examines energy cost during operation, it does not include capital or other operations and maintenance costs.
Version 1.1 update: Reference Tab, Cell C19 changed from 499.30 to 241.175 to correctly use kg instead of pounds.
Disclaimer:
This tool makes considerable simplifications about the operational performance of heat pumps to further the goal of informing a wide range of audiences on the general range of heat pump performance. Heat pump sizing and accompanying system design should be conducted by an experienced design professional familiar with brewery operations. Simplifications include but are not limited to:
- Assumes heat pump operates at the user input COP, with no accounting for seasonal or other variations that will affect heat pump performance.
-Assumes a 50% load factor for ASWHPWH and SGHP in the absence of actual energy use data in the tool
-Assumes energy costs based on EIA data. Users can adjust as needed in the Comparison Cals tab.
-Password to disable sheet protection: password

## Introduction
CalNext Craft Brewery Screening Tool
Heat Pumps by Brewery Process
The diagram below shows the various potential applications for the three main heat pump technologies considered in this tool (ASHPWH, HTHP, HRC). The three green boxes represent the heat pump technologies included in this screening tool. Blue boxes and arrows represent heat sources, red arrows and boxes denote end uses (heat sinks).
Figure 2, Decision and Equipment Evaluation Data Flow Charts.
Click image to be taken to a larger image for easier viewing
Figure 1, Heat Sources, Heat Sinks, and Equipment Types
Click image to be taken to a larger image for easier viewing

## Comparison Calcs
CalNext Craft Brewery Screening Tool
Main Calculation Tool
Color Coding Legend
User Input
Intermediate Calculated Value
Output Calculation result
Final output
| Inputs |  |  |  | Outputs
Energy Costs
| Variables | Default Value (EIA 7/2024) | Values
| Natural Gas dollars per therm | 1.42 | 1.42
| Electricity dollar per kilowatt-hour | 0.237 | 0.24 |  |  |  |  | Air Source Heat Pump Water Heater
[5 empty] | Hourly Outputs |  |  |  | Per Barrel and Annual Outputs
| Air Source Heat Pump Water Heater |  |  |  | Energy Input |  | Cost
| Variables | Usage | Values |  | Variables | Values | Variables | Values | Variables | Natural Gas (therms) | Electricity (kWh)
| Annual Hours of Operation | Per Barrel and Annual Outputs | 1000 |  | Natural Gas (therm) | 2.5006 | Natural Gas | 3.5509 | Energy per Barrel | 2.0005 | 16.9283
| Annual Production (barrels) | Per Barrel and Annual Outputs | 1250 |  | Electricity Heat Pump (kWh) | 21.1604 | Electricity Heat Pump | 5.0785 | Cost per Barrel | 2.8407 | 4.0628
| Water Heater Size (kBTU/hour) | Hourly Outputs | 500 | [5 empty] | Annual Energy | 2500.6058 | 21160.361
| Water Heater Efficiency (%) | Hourly Outputs | 80% |  | Emissions (kg CO2) |  |  |  | Annual Cost | 3550.8602 | 5078.4866
| Heat Pump Water Heater COP | Hourly Outputs | 2.77 |  | Variables | Values
| Equipment Average Load | Hourly Outputs | 50% |  | Natural Gas | 13.2682
[5 empty] | Electricity Heat Pump | 5.1034
Steam Generating Heat Pump
[5 empty] | Hourly Outputs |  |  |  | Per Barrel and Annual Outputs
Energy Input
| Steam Generating Heat Pump |  |  |  | Variables | Values | Cost |  | Variables | Natural Gas (therms) | Electricity (kWh)
| Variables | Usage | Values |  | Natural Gas (therm) | 8.372 | Variables | Values | Energy per Barrel | 6.6976 | 58.1452
| Steam Generating Heat Pump COP | Hourly Outputs | 2.7 |  | Electricity Heat Pump (kWh) | 72.6815 | Natural Gas | 11.8883 | Cost per Barrel | 9.5106 | 13.9548
| Boiler Size (BHP) | Hourly Outputs | 50 |  |  |  | Electricity Heat Pump | 17.4436 | Annual Energy | 8372.0137 | 72681.4815
| Annual Hours of Operation | Per Barrel and Annual Outputs | 1000 |  | Emissions (kg CO2) |  |  |  | Annual Cost | 11888.2594 | 17443.5556
| Annual Production (barrels) | Per Barrel and Annual Outputs | 1250 |  | Variables | Values
| Boiler Efficiency | Hourly Outputs | 80% |  | Natural Gas | 44.4219
| Equipment Average Load | Hourly Outputs | 50% |  | Electricity Heat Pump | 17.529
Heat Recovery Chiller
[5 empty] | Batch Outputs |  |  |  | Per Batch and Annual Outputs
[5 empty] | Energy Input |  | Cost
| Heat Recovery Chiller |  |  | Check Values! A Value or A Combination of Values Results in Invalid Calculation (negative COP) | Variables | Values | Variables | Values | Variables | Natural Gas (therms) | Electricity (kWh)
| Variables | Usage | Values |  | Natural Gas (therm) | 9.814 | Natural Gas | 13.9358 | Energy per Barrel | 0.09814 | 0.35354
| Annual Production (barrels) | Per Barrel and Annual Outputs | 2000 |  | Electricity Heat Pump (kWh) | 35.3537 | Electricity Heat Pump | 8.4849 | Cost per Barrel | 0.13936 | 0.084849
| Starting Temperature (°F) | Batch outputs | 180 | [5 empty] | Annual Energy | 196.2791 | 707.0747
| Target Temperature (°F) | Batch outputs | 200 |  | Emissions (kg CO2) |  |  |  | Annual Cost | 278.7164 | 169.6979
| Hot Water Volume (BBL) | Batch outputs | 100 |  | Variables | Values
| Time (minutes) | Batch outputs | 60 |  | Natural Gas | 52.0729
| Cooling water Temperature (°F) | Batch outputs | 170 |  | Electricity Heat Pump | 8.5264
| Cooling water Volume (BBL) | Batch outputs | 100 | [5 empty] | Variables | Value
[9 empty] | Cooled water ending Temperature | #N/A
For this screening tool, applications of IHPs in craft breweries are subdivided into three main end uses: water heating, steam generation, and heat recovery/chilling. The three end uses also generally correspond to three types of industrial heat pumps. For water heating, the project team considered air source heat pump water heaters (ASHPWH), for steam generation, steam generating heat pumps (SGHP), and for heat recovery/chilling, heat recovery chillers.
To use this tool, take the following steps:
Step 1. Input energy costs. Suggested values are provided based on EIA averages, but the outputs will be more accurate if you enter your own average rates
Step 2. Select the technology that you are interested in. Choose between air source heat pump water heater, steam generating heat pump or heat recovery chiller.
Step 3. Enter the relevant inputs based on your brewing facilities and operations.
Step 4. Review the outputs to understand the impacts of the heat pump technology.
Step 5. Visit the individual equipment chapters (ASHPWH, SGHP, Heat Recovery) for a more detailed look at calculations. For instance, this main calculator assumes an average equipment load of 50%, which can be adjusted in the ASHPWH and SGHP tabs if so desired.
Reset calculator to default values

## Reference
CalNext Craft Brewery Screening Tool
References and values used for calculations
Performance Assumptions
| Variable | Value | Link
| Delta_T_Approach (K) | 11.111 | DOE-EERE
| Actual COP (%) | 70% | DOE-EERE
| Steam Efficiency (%) | 52.7% | Inveno Engineering
| Boiler Efficiency (%) | 83.6% | Inveno Engineering
Emissions
| Variable | Value | Link
| Emissions kg CO2 /MWh | 241.175 | eGRID
| Emissions kg CO2/ kWh | 0.24118 | derived from eGrid
| Emissions kg CO2/mmBTU | 53.06 | eGRID
| Emissions kg CO2 /therm | 5.306 | derived from eGrid
Energy Cost
| Variable | Value | Link
| Electricity Cost per kWh ($) | 0.24 | EIA - Commercial
| NG Cost per Mcf ($) | 14.74 | EIA
| NG Cost per therm ($) | 1.42 | derived from EIA
Conversions and Miscellaneous Assumptions
| Variable | Value
| °C to K | 273.15
| °R to °F | 458.67
| liters per gallon | 3.7854
| liters per barrel | 117.348
| gallons per barrel | 31
| btu per kWh | 3412
| kWh per therm | 29.3
| btu per therm | 99976.1
| kJ per kWh | 3600
| kJ per therm | 105480
| btuh per boiler hp | 33475
| btu per kJ | 0.948
| boiler hp to kW | 9.812
| kW per BTUh | 0.29307
| kW to kWh | 1
| therm per Mcf | 10.38
| kj per kwh | 3600
| heat capacity H2O (kJ/kg*K) | 4.184
| Density water (lb/gal) | 8.334
Drop down menus
| Variable | Value
Load factor time period
Batch
Month
Year
| Load Factor Calculation Source | %
| Default Estimate | 50%
Bill Data Calculation
Meter Data Calculation
Variable Cell References
| Variable Name | Location in Spreadsheet
| Actual_COP_percent_of_ideal | =Reference!$C$13
| Boiler_Efficiency | =Reference!$C$15
| boiler_hp_per_kW | =Reference!$C$45
| btu_per_kJ | =Reference!$C$44
| btuh_per_boiler_hp | =Reference!$C$43
| Cp_H2O | =Reference!$C$50
| Electricity_Cost_per_kWh | =Reference!$C$26
| HP_approach_temp | =Reference!$C$12
| K_to_C | =Reference!$C$33
| kg_CO2_per_kWh | =Reference!$C$20
| kg_CO2_per_therm | =Reference!$C$22
| kj_per_kwh | =Reference!$C$49
| kJ_per_therm | =Reference!$C$42
| kW_per_BTUh | =Reference!$C$46
| kW_to_kWh | =Reference!$C$47
| liters_per_barrel | =Reference!$C$36
| NG_Cost_per_therm | =Reference!$C$28
| steam_efficiency | =Reference!$C$14
| therm_per_Mcf | =Reference!$C$48
| Actual_COP_percent_of_ideal | =Reference!$C$13
| Boiler_Efficiency | =Reference!$C$15
| boiler_hp_per_kW | =Reference!$C$45
| Boiler_Size__BHP | =ASHPWH!$B$39
| btu_per_kJ | =Reference!$C$44
| btuh_per_boiler_hp | =Reference!$C$43
| Cp_H2O | =Reference!$C$50
| Electricity_Cost_per_kWh | =Reference!$C$26
| Electricity_Heat_Pump__kWh | =ASHPWH!$B$56
| Heat_Pump_COP | =ASHPWH!$B$40
| Heat_pump_input_required_kW | =ASHPWH!$B$106
| HP_approach_temp | =Reference!$C$12
| K_to_C | =Reference!$C$33
| kg_CO2_per_kWh | =Reference!$C$20
| kg_CO2_per_therm | =Reference!$C$22
| kj_per_kwh | =Reference!$C$49
| kJ_per_therm | =Reference!$C$42
| kW_per_BTUh | =Reference!$C$46
| kW_to_kWh | =Reference!$C$47
| liters_per_barrel | =Reference!$C$36
| Natural_Gas__therm | =ASHPWH!$B$55
| NG_Cost_per_therm | =Reference!$C$28
| steam_efficiency | =Reference!$C$14
| therm_per_Mcf | =Reference!$C$48
| Water_Heater_Efficiency | =ASHPWH!$B$39
| Water_Heater_output__kJ__per_hour | =ASHPWH!$B$107
| Water_Heater_size_in__kW | =ASHPWH!$B$104
| Water_Heater_size_kBTUh | =ASHPWH!$B$38
| water_heater_useful_output_kW | =ASHPWH!$B$105
| Actual_COP_percent_of_ideal | =Reference!$C$13
| Boiler_Efficiency | =Reference!$C$15
| boiler_hp_per_kW | =Reference!$C$45
| Boiler_Size__BHP | =SGHP!$B$37
| boiler_size_in__kW | =SGHP!$B$106
| Boiler_useful_output__kW | =SGHP!$B$107
| btu_per_kJ | =Reference!$C$44
| btuh_per_boiler_hp | =Reference!$C$43
| Cp_H2O | =Reference!$C$50
| Electricity_Cost_per_kWh | =Reference!$C$26
| Heat_Pump_COP | =SGHP!$B$39
| Heat_pump_input_required__kW | =SGHP!$B$108
| Heat_pump_kwh | =SGHP!$B$53
| HP_approach_temp | =Reference!$C$12
| K_to_C | =Reference!$C$33
| kg_CO2_per_kWh | =Reference!$C$20
| kg_CO2_per_therm | =Reference!$C$22
| kilojoule_per_hour | =SGHP!$B$109
| kJ_per_hour | =SGHP!$B$109
| kj_per_kwh | =Reference!$C$49
| kJ_per_therm | =Reference!$C$42
| kW_per_BTUh | =Reference!$C$46
| kW_to_kWh | =Reference!$C$47
| liters_per_barrel | =Reference!$C$36
| Natural_gas_therm | =SGHP!$B$52
| NG_Cost_per_therm | =Reference!$C$28
| steam_efficiency | =Reference!$C$14
| therm_per_Mcf | =Reference!$C$48
| Actual_COP_percent_of_ideal | =Reference!$C$13
| Boiler_Efficiency | =Reference!$C$15
| boiler_hp_per_kW | =Reference!$C$45
| Boiler_size_BHP | ='Heat Recovery'!$E$39
| btu_per_kJ | =Reference!$C$44
| btuh_per_boiler_hp | =Reference!$C$43
| Cooled_Water_Volume__bbl | ='Heat Recovery'!$E$24
| Cooling_Calculated_Ending_Water_Temperature__°F | ='Heat Recovery'!$E$27
| Cooling_Starting_Water_Temperature__°F | ='Heat Recovery'!$E$23
| COP_estimate | ='Heat Recovery'!$H$69
| Cp_H2O | =Reference!$C$50
| Electricity_Cost_per_kWh | =Reference!$C$26
| heat_pump_T_in__°C | ='Heat Recovery'!$H$66
| heat_pump_T_out__°C | ='Heat Recovery'!$H$67
| heat_sink_calculated_flow_rate_gpm | ='Heat Recovery'!$B$74
| heat_sink_calculated_Time_minutes | ='Heat Recovery'!$B$73
| heat_sink_delta_T°F | ='Heat Recovery'!$B$71
| heat_sink_Flow_rate__gpm | ='Heat Recovery'!$B$30
| heat_sink_Flow_Rate__lpm | ='Heat Recovery'!$B$75
| heat_sink_Hot_Water_Volume__bbl | ='Heat Recovery'!$B$28
| heat_sink_Mass_flow__kg_s | ='Heat Recovery'!$B$77
| heat_sink_Q_in__kW__kJ_s | ='Heat Recovery'!$B$78
| Heat_sink_Temp_in | ='Heat Recovery'!$B$66
| Heat_sink_Temp_out | ='Heat Recovery'!$B$68
| heat_sink_Total_Energy__kJ | ='Heat Recovery'!$B$79
| heat_sink_total_mass_kg | ='Heat Recovery'!$B$76
| heat_sink_total_volume_bbl | ='Heat Recovery'!$B$72
| heat_sinkdelta_T | ='Heat Recovery'!$B$70
| heat_source_Ending_Energy | ='Heat Recovery'!$E$70
| heat_source_Ending_Temperature__°C | ='Heat Recovery'!$E$71
| heat_source_Ending_Temperature__°F | ='Heat Recovery'!$E$72
| heat_source_Starting_energy | ='Heat Recovery'!$E$69
| heat_source_T_in__°C | ='Heat Recovery'!$E$66
| heat_source_Total_Mass__kg | ='Heat Recovery'!$E$68
| Heating_Desired_Water_Temperature__°F | ='Heat Recovery'!$B$24
| Heating_Starting_Water_Temperature__°F | ='Heat Recovery'!$B$23
| HP_approach_temp | =Reference!$C$12
| K_to_C | =Reference!$C$33
| kg_CO2_per_kWh | =Reference!$C$20
| kg_CO2_per_therm | =Reference!$C$22
| kj_per_kwh | =Reference!$C$49
| kJ_per_therm | =Reference!$C$42
| kW_per_BTUh | =Reference!$C$46
| kW_to_kWh | =Reference!$C$47
| liters_per_barrel | =Reference!$C$36
| Natural_gas_therm | ='Heat Recovery'!$B$40
| NG_Cost_per_therm | =Reference!$C$28
| steam_efficiency | =Reference!$C$14
| Temperature_Difference__°F | ='Heat Recovery'!$B$25
| therm_per_Mcf | =Reference!$C$48
| Time__minutes | ='Heat Recovery'!$B$29
| W_in__kW | ='Heat Recovery'!$H$70
This page includes references for values and assumptions used in the tool's calculations. Details of these variables are covered in the data dictionary. For those interested in understanding in-spreadsheet cell references, refer to the table at the bottom of this page.

## Data Dictionary
CalNext Craft Brewery Screening Tool
Data Dictionary
Sheet | Section | Table | Variable | Description | Units
Reference | Values used for calculations | System Performance Assumptions | Delta_T_Approach | The approach temperature for the heat pump working fluid | Kelvin
|  |  | Actual COP % | Factor used to reduce ideal COP to estimated COP | %
|  |  | Steam System Efficiency | Estimated efficiency of a steam system from generation through delivery to end use | %
|  |  | Boiler Efficiency | Estimated boiler efficiency for steam generation | %
|  | Emissions | Emissions kg CO2 /MWh | CO2 emissions per mega watt hour of electrical energy | kg CO2/MWh
|  |  | Emissions kg CO2/ kWh | CO2 emissions per kilowatt hour of electrical energy | kg CO2/MWh
|  |  | Emissions kg CO2/mmBTU | CO2 emissions per million British Thermal Units of Natural gas | kg CO2/mmBTU
|  |  | Emissions kg CO2 /therm | CO2 emissions per therm of natural gas | kg CO2/therm
|  | Energy Cost | Electricity Cost per kWh ($) | Electricity Cost per kilowatt hour for California | $
|  |  | NG Cost per Mcf ($) | Natural gas cost per thousand cubic feet for California | $
|  |  | NG Cost per therm ($) | Natural gas cost per therm for California | $
|  | Conversions | °C to K | Converting between Celsius and Kelvin | N/A
|  |  | °R to °F | Converting between Fahrenheit and Rankine | N/A
|  |  | liters per gallon | Converting between liters and gallons | N/A
|  |  | liters per barrel | Converting between liters and barrels | N/A
|  |  | gallons per barrel | Converting between gallons and barrels | N/A
|  |  | btu per kWh | Converting between British thermal units and kilowatt hours | N/A
|  |  | kWh per therm | Converting between kilowatt hours and therms | N/A
|  |  | btu per therm | Converting between British thermal units and therms | N/A
|  |  | kJ per kWh | Converting between kilojoules and kilowatt hours | N/A
|  |  | kJ per therm | Converting between kilojoules and therms | N/A
|  |  | BTUh per boiler hp | Converting between British thermal units per hour and boiler horsepower | N/A
|  |  | BTU per kJ | Converting between British thermal units per hour and kilojoules | N/A
|  |  | boiler hp to kW | Converting between boiler horsepower and kilowatts | N/A
|  |  | kW per BTUh | Converting between kilowatt hours and British thermal units | N/A
|  |  | kW to kWh | Converting between kilowatts in one hour to kilowatt hours | N/A
|  |  | therm per Mcf | Converting between therms and thousand cubic feet of natural gas | N/A
|  |  | kj per kwh | Converting between kilojoule and kilowatt hour | N/A
|  |  | heat capacity H2O (kJ/kg*K) | Isobaric specific heat of water | kJ/kg*K
|  |  | Density water (lb/gal) | Density of water at 68°F | lb/gal
|  | Water Heater Inputs | Water Heater Size | Size of existing water heater | kBTU
|  |  | Water heater efficiency | Efficiency of the existing water heater | %
|  |  | Heat Pump Water heater COP | Coefficient of performance for the heat pump water heater under consideration | N/A
ASHPWH | Calculator Inputs | Production Data | Annual Hours of operation | Annual operational hours of existing heat pump water heater | hours
|  |  | Annual Production | Annual beer production | Barrels
|  | Per Barrel Outputs | Energy Use per Barrel of water heated | Energy used per barrel of water heated in therms or kWh depending on technology type | therms/kWh
|  |  | Cost per Barrel of water heated | Cost of energy per barrel of water heated | $/barrel
|  | Annual Outputs | Annual Estimate Energy | Annual estimate of energy used from inputted annual production data | therms/kWh
| Calculator Outputs | Hourly Outputs | Energy Input | Energy used per batch of water heated | therms/kWh
|  |  | Emissions | Estimated CO2 emissions from the consumption of each energy type per batch of water heated | kg CO2
|  |  | Energy Cost | Estimated cost of the energy used per batch for each technology type | $/therm or $/kWh
|  | Boiler Inputs | Boiler Size | Size of existing boiler | Boiler Horsepower
|  |  | Steam Generating Heat Pump COP | Coefficient of performance for the steam generating heat pump under consideration | N/A
|  | Production Data | Annual Hours of operation | Annual operational hours of existing heat pump water heater | hours
SGHP | Calculator Inputs |  | Annual Production | Annual beer production | Barrels
|  | Per Barrel Outputs | Energy Use per Barrel of water heated | Energy used per barrel of water heated in therms or kWh depending on technology type | therms/barrel or kWh/barrel
|  |  | Cost per Barrel of water heated | Cost of energy per barrel of water heated | $/barrel
|  | Annual Outputs | Annual Estimate Energy | Annual estimate of energy used from inputted annual production data | therms/kWh
| Calculator Outputs | Hourly Outputs | Energy Input | Energy used per batch of water heated | therms/kWh
|  |  | Emissions | Estimated CO2 emissions from the consumption of each energy type per batch of water heated | kg CO2
|  |  | Energy Cost | Estimated cost of the energy used per batch for each technology type | $/batch
|  | Water Heating Temperatures | Starting Water Temperature (°F) | Starting temperature of water to be heated | Fahrenheit
|  |  | Desired Water Temperature (°F) | Desired temperature of water when heating is completed | Fahrenheit
|  | Water Heating Volume and Time | Hot water Volume | Volume of water to be heated from starting temperature to desired temperature | Barrels
Heat Recovery | Calculator Inputs |  | Time | Desired duration of heating | Minutes
|  | Production Data | Annual Production | Annual production of brewery | Barrels
|  | Water Cooling Temperature and Volume | Strating water temperature (°F) | Starting temperature of water to be cooled | Fahrenheit
|  |  | Cooled Water Volume (bbl) | Volume of water to be cooled | Barrels
|  | Per Barrel Outputs | Energy Use per Barrel of water heated | Energy used per barrel of water heated in therms or kWh depending on technology type | therms/barrel or kWh/barrel
|  |  | Cost per Barrel of water heated | Cost of energy per barrel of water heated | $/barrel
|  | Annual Outputs | Annual Estimate Energy | Annual estimate of energy used from inputted annual production data | therms or kWh
| Calculator Outputs |  | Annual Estimate Cost | Estimate of annual energy cost from inputted annual production data | $
|  | Per Batch Outputs | Energy Input | Energy used per batch of water heated | therms/barrel or kWh/barrel
|  |  | Emissions | Estimated CO2 emissions from the consumption of each energy type per batch of water heated | kg CO2
|  |  | Energy Cost | Estimated cost of the energy used per batch for each technology type | $/batch
|  | Heat Sink | T_in | Temperature of incoming water to be heated | Celsius or Fahrenheit
|  |  | T_out | Temperature of incoming water after heating | Celsius or Fahrenheit
|  |  | delta_T | Difference between water temperature after heating and before heating | Celsius or Fahrenheit
|  |  | Total_Volume | Total volume of water being heated | Barrels
|  |  | Time | Total time for volume of water to be heated | Minutes
|  |  | Flow rate | Volumetric flowrate of water to be heated | gpm or lpm
|  |  | Total Mass | Total mass of water to be heated | kg
|  |  | Mass_flow | Mass flow rate of water to be heated | kg/s
|  |  | Q_in | Energy input into the water to be heated to desired temperature | kW
|  |  | Total Energy | Total energy required to heat the volume of water from incoming temperature to desired temperature | kJ
|  | Heat Source | T_in | Incoming temperature of water to be cooled | Celsius or Fahrenheit
|  |  | Flowrate | Volumetric flowrate of water to be cooled | gpm
|  |  | Total Mass | Total mass of water to be cooled | kg
|  |  | Starting Energy | Total energy of mass of water to be cooled at starting temperature | kJ
|  |  | Ending Energy | Total energy of mass of water to be cooled after energy for heating water has been extracted | kJ
|  |  | Ending Temperature | Final temperature of water to be cooled after energy for heating water has been extracted | Celsius or Fahrenheit
|  | Heat Recovery Chiller | T_in | Inlet temperature of heat recovery chiller working fluid | Celsius
|  |  | T_out | Outlet temperature of heat recovery chiller working fluid | Celsius
|  |  | COP_ideal | Ideal Coefficient of performance using working fluid temperatures | N/A
|  |  | COP_estimate | Estimated Coefficient of performance after accounting for below ideal equipment performance | N/A
|  |  | W_in | Electrical power input into the heat recovery chiller | kW
|  |  | Q_out | Power out of the heat recovery chiller from the cooled water to the heated water | kW
This tab provides a descriptions for all variables used in the spreadsheet, organized by sheet, section, and table.

## ASHPWH
CalNext Craft Brewery Screening Tool
Air Source Heat Pump Water Heater
Color Coding Legend
User Input
Intermediate Calculated Value
Output Calculation result
Final output
Load Estimate (Read Instructions in Cells A21 and D21)
Equipment average load estimate (meter data) |  | Equipment average load estimate (bill data)
Gas Meter Start Reading | 1000 | Bill Hours of Runtime | 1
Starting Time | 2024-03-02 23:30 | Monthly gas use (therms) | 3
Gas Meter End Reading | 1010 | Percent of Monthly Gas Use | 90%
Ending Time | 2024-03-03 02:30 | Monthly gas use kBTU | 299.9283
Billing Factor | 1.1 | Average hourly gas use | 269.9355
Hours of Operation | 3 | Boiler output kBTU/hour | 500
Energy Use (therms) | 10 | Average Load estimate (bill data) | 53.99%
Energy Use (kBTU/hour) | 333.2537
Boiler Output (kBTU/hour) | 500
Average Load Estimate (meter data) | 66.65%
Calculator Inputs
Equipment Data
Water Heater size kBTU | 500
Water Heater Efficiency | 80%
Heat Pump COP | 2.77
Production Data
Annual Hours of Operation | 1000
Annual Production (barrels) | 1250
Average Load Calculation Source | Default Estimate
Average Load (%) | 50%
Calculator Outputs
Hourly Impacts
| Energy Input |  | Cost
Natural Gas (therm) | 2.5006 | Natural Gas | 3.5509
Electricity Heat Pump (kWh) | 21.1604 | Electricity Heat Pump | 5.0785
Emissions (kg CO2)
Natural Gas | 13.2682
Electricity Heat Pump | 5.1034
Annual & Per Barrel Estimates
Per Barrel Impacts
| Energy Input |  | Cost
Natural Gas (therm) | 2.0005 | Natural Gas | 2.8407
Electricity Heat Pump (kWh) | 16.9283 | Electricity Heat Pump | 4.0628
Emissions (kg CO2)
Natural Gas | 10.6146
Electricity Heat Pump | 4.0827
Annual Impacts
| Energy Input |  | Cost
Natural Gas (therm) | 2500.6058 | Natural Gas | 3550.8602
Electricity Heat Pump (kWh) | 21160.361 | Electricity Heat Pump | 5078.4866
Emissions (kg CO2)
Natural Gas | 13268.2144
Electricity Heat Pump | 5103.3501
Miscellaneous Heat Pump Assumptions
Variable Name | Values
Water Heater size converted to kW | 146.5355
Water Heater Useful Output (kW) | 117.2284
Estimated Heat Pump Input (kW) | 42.3207
Water Heater output (kJ) per hour | 527527.8
Water Heater output (kJ) per hour | 422022.24
This tab compares the performance of an air source heat pump water heater to a conventional natural gas water heater. The default water heater efficiency is for a several year old standard efficiency water heater. For the heat pump it is assumed that the required heat source input conditions can be met, that heat pump is of comparable size to the water heater, and that heat pump can output water at the required temperature. The default heat pump value is for a Trane Ascend air source heat pump. For details on user inputs, click on each default value for guidance.

## SGHP
CalNext Craft Brewery Screening Tool
Air Source Heat Pump Water Heater
Color Coding Legend
User Input
Intermediate Calculated Value
Output Calculation result
Final output
Load Estimate (Read Instructions in Cells A21 and D21)
Equipment average load estimate (meter data) |  | Equipment average load estimate (bill data)
Gas Meter Start Reading | 1000 | Estimated hours of boiler run time of the month | 25
Starting Time | 2024-03-02 23:30 | Monthly gas use (therms) | 300
Gas Meter End Reading | 1020 | Percent of Monthly Gas Use | 90%
Ending Time | 2024-03-03 01:30 | Monthly gas use kBTU | 29992.83
Billing Factor | 1.1 | Average hourly gas use | 1079.7419
Hours of Operation | 2 | Boiler output kBTU/hour | 1673.75
Energy Use (therms) | 20 | Average Load estimate (bill data) | 64.51%
Energy Use (kBTU/hour) | 999.761
Boiler Output (kBTU/hour) | 1673.75
Average Load Estimate (meter data) | 59.73%
Calculator Inputs
Equipment Data
Boiler Size (BHP) | 50
Boiler Efficiency | 80%
Heat Pump COP | 2.7
Production Data
Hours of Steam Boiler Operation | 1000
Annual Production (BBL) | 1250
Average Load Calculation Source | Default Estimate
Average Load (%) | 50%
Calculator Outputs
Estimated Hourly Impacts
| Energy Input |  | Cost
Natural Gas (therm) | 8.372 | Natural Gas | 11.8883
Electricity Heat Pump (kWh) | 72.6815 | Electricity Heat Pump | 17.4436
Emissions (kg CO2)
Natural Gas | 44.4219
Electricity Heat Pump | 17.529
Annual & Per Barrel Estimates
Per Barrel Impacts
| Energy Input |  | Cost
Natural Gas (therm) | 6.6976 | Natural Gas | 9.5106
Electricity Heat Pump (kWh) | 58.1452 | Electricity Heat Pump | 13.9548
Emissions (kg CO2)
Natural Gas | 35.5375
Electricity Heat Pump | 14.0232
Annual Impacts
| Energy Input |  | Cost
Natural Gas (therm) | 8372.0137 | Natural Gas | 11888.2594
Electricity Heat Pump (kWh) | 72681.4815 | Electricity Heat Pump | 17443.5556
Emissions (kg CO2)
Natural Gas | 44421.9044
Electricity Heat Pump | 17528.9563
Miscellaneous Assumptions and Variables
Miscellaneous Heat Pump and Boiler Assumptions
Variable Name | Values
Boiler Size Converted to kW | 490.6
Boiler Useful Output (kW) | 392.48
Heat Pump Input Required (kW) | 145.363
Boiler Size kJ/hr | 1766160
Note on A105: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jose recommended remove
Steam Generating heat pumps require a heat source to operate. For potential heat sources that may be found in a brewery, refer to Figure 1 on the introduction tab. This tab compares the generation of steam with a steam generating heat pump to a typical natural gas fired boiler. A boiler efficiency of 83.6% was used (Inveno Engineering, 2019) for a well maintained boiler. For the heat pump, we assumed that the steam is low pressure steam, that the required heat source input conditions are able to be supplied for either water source or air source heat pumps, and that the heat pump can output at the required steam pressure. The default value is for a Kobelco SGHP which gives a COP of 2.7 with a 45°C (water) heat source. For 55°C heat source the COP is 3.1, and for 65°C heat source the COP is 3.3. For details on user inputs, click each default value for guidance.

## Heat Recovery
CalNext Craft Brewery Screening Tool
Heat Recovery
Color Coding Legend
User Input
Intermediate Calculated Value
Output Calculation result
Final output
Calculator Inputs
Water Heating Temperatures |  |  | Water Cooling Temperature and Volume
Starting Water Temperature (°F) | 180 |  | Starting Water Temperature (°F) | 170
Desired Water Temperature (°F) | 200 |  | Cooled Water Volume (bbl) | 100
Water Heating Volume and Time |  |  | Calculated Ending Water Temperature (°F) | #N/A
Hot Water Volume (bbl) | 100
Time (minutes) | 60
Production Data
Annual Production (BBL) | 2000
Calculator Outputs
Per Batch Impacts
Energy Input
Natural Gas | 9.814
Electricity Heat Pump | 35.3537
| Emissions (kg CO2) |  |  | Energy Cost
Natural Gas | 52.0729 |  | Natural Gas | 13.9358
Electricity Heat Pump | 8.5264 |  | Electricity Heat Pump | 8.4849
Per Barrel Impacts
| Steam Boiler | Heat Recovery Chiller
Energy Use per Barrel of water heated | 0.09814 | 0.35354
Cost per Barrel of water heated | 0.13936 | 0.084849
Annual Impacts
| Steam Boiler | Heat Recovery Chiller
Annual Estimate Energy | 196.2791 | 707.0747
Annual Estimate Cost | 278.7164 | 169.6979
Annual Emission Estimate | 1041.457 | 170.5287
Miscellaneous Assumptions and Variables
Heat Sink |  |  | Heat Source |  | Heat Recovery Chiller
Variable Name | Value |  | Variable Name | Value | Variable Name | Value
T_in (°C) | 82.2222 |  | T_in (°C) | #N/A | T_in (°C) | #N/A
T_in (°F) | #N/A |  | Flow_Rate (gpm) | 51.6667 | T_out (°C) | 104.4443
T_out (°C) | 93.3333 |  | Total Mass (kg) | 11734.8 | COP_ideal | #N/A
T_out (°F) | #N/A |  | Starting energy (kJ) | #N/A | COP_estimate | 5.2863
delta_T (°C) | #N/A |  | Ending Energy (kJ) | 16629901.9327 | W_in (kW) | 35.3537
delta_T (°F) | #N/A |  | Ending Temperature (°C) | 65.5556 | Q_out (kW) | 186.892
Total Volume (bbl) | 100 |  | Ending Temperature (°F) | #N/A
Time (minutes) | 60
Flow_Rate (gpm) | 51.6668
Flow_Rate (lpm) | 195.58
Total Mass (kg) | 11734.8
Mass_flow (kg/s) | 3.2597
Q_in (kW (kJ/s)) | 151.5383
Total Energy (kJ) | 545537.8133
This tab lets users explore how the water heating and cooling parameters such as temperature and volume of both heat source and heat sink affect heat recovery chiller performance and operating cost while comparing to a traditional steam boiler system. The Coefficient of Performance is automatically calculated based upon the desired water temperature for water heating and the starting temperature of the cooling water. The calculations used follow the format used by the U.S. Department of Energy's Energy Efficiency and Renewable Energy Brief: Industrial Heat Pumps for Steam and Fuel Savings (2003).

## Other EE Measures
CalNext Craft Brewery Screening Tool
Heat Recovery
Estimated Savings and Paybacks for Energy Efficiency Measures
| Primary Energy/Measure | Payback | Savings
| (Process specific) | (Years) | kBTU/Barrel
Boilers and Steam Distribution
| Maintenance | <1 | 4
| Improved process control | <1 | 3
| Flue gas heat recovery | >3 | 2
| Blowdown steam recovery | 2.7 | 2 to 3
| Steam trap maintenance | <1 | 3.4
| Automatic steam trap monitoring | <1 | <1
| Leak repair | <1 | 6
| Condensate return | >1 | 19 to 21
| Insulation of steam pipes | 1 | 6 to 28
| Process integration |  | 47 to 84
Motors and Systems using Motors
| Variable speed drives | 2 to 3 | 6 to 25
| Downsizing | 2 | 1 to 2
| High efficiency | 1 to 2 | 1 to 2
Refrigeration and Cooling
| Better matching of cooling capacity and loads | 3.6 | 1 to 2
| Improved operation of ammonia cooling system | 5.5 | <1 to 2
| Improved operations and maintenance | <1 | 4
| System modifications and improved design | <3 | 5 to 8
| Insulation of cooling lines | n/a | limited data
Other Utilities
| Lighting | <2 to 3 | 2 to 6
| Reduce space heating demand | n/a | 8
| Membrane filtration wastewater | <5 | limited data
| Control and monitoring systems | <1 to 5 | <1 to 37
Mashing and Lauter Tun
| Waste heat recovery | n/a | limited data
| Use of compression filter | 2 | 19
Wort Boiling and Cooling
| Vapor condensers | <2 to 5 | <1 to 22
| Thermal vapor recompression | >2 | 16 to 18
| Mechanical vapor recompression |  | 23
| High gravity brewing | <1 | 13 to 22
| Low pressure wort boiling | n/a | 32 to 40
| Wort stripping | n/a | 20 to 42
| Wort cooling | 3 | 17
Fermentation
| Immobilized yeast fermenter | n/a | limited data
| Heat recovery | >2 | limited data
| New CO2 recovery systems | >2 | limited data
Processing
| Microfiltration | 2 to 4 | limited data
| Membranes | 4 | 19
| Heat recovery-pasteurization | n/a | 1
| Flash pasteurization | n/a | 6 to 14
Packaging
| Heat recovery washing | 3 | 6
| Cleaning improvements | 3.4 | 23
This tab contains preliminary payback and process specific unit savings based on a 2002 LBNL study on energy efficiency opportunities in the brewing industry. While this study is old, this list suggests options for brewers either in addition to heat pump installation or as a complement to it. Check with your local utility and 3rd party program implementer for potential incentives and On-Bill Financing.

## Figure 1
Blue Boxes represent heat sources
Magenta boxes represent heat sinks
Green boxes represent technologies
Blue arrows represents heat flowing from a source to an equipment
Red arrows represent heat flowing from an equipment to a heat sink (end use).
Brewing process diagram courtesy "Opportunities for energy efficiency improvements in craft and micro-breweries" Raffa, Bennett, Clemon ASME 2022
Figure 1, Heat Sources, Heat Sinks, and Equipment Types
Click image to return to Introduction Tab

## Figure 2
Figure 2, Decision and Equipment Evaluation Data Flow Charts.
Click image to return to Introduction Tab